Assessors Judgment Guide

| Qualification | National Diploma Level-5 in Telecommunication Technology Basic Electrical Engineering |
| --- | --- |
| Competency Standard(s) | 0714-E&A-3: Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence |
| Candidate Details | Name:_______ _______________________________________ Registration/Roll Number: ________________________ Signature: ____________________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor________________________ Assessor’s code:___________________ Signature:__________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Measure single phase power using Volt-Ampere meter method - Measure single phase power using watt meter - Measure 3 phase power with watt meter - Measure power with two-watt meters - Measure power with three-watt meters - Measure consumed energy with Energy meter - Measure power factor with voltmeter, ampere meter and watt meter - Measure power factor with power factor meter - Improve power factor & measure it with power factor meter - Determine phase sequence with phase sequence meter |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Select a proper load to calculate the power and give supply to it. |  |  |  |  |  |
|  | Measure the voltage and current by using voltmeter and ampere meter. |  |  |  |  |  |
|  | Find power using power formula. |  |  |  |  |  |
|  | Select a proper load to calculate the power and connect watt meter with it. |  |  |  |  |  |
|  | Give supply and measure the reading of power. |  |  |  |  |  |
|  | Connect current coil of watt meter in series to any phase and one terminal of balance load. |  |  |  |  |  |
|  | Connect voltage coil of watt meter to that phase and neutral |  |  |  |  |  |
|  | Give 3-phase supply to load and take reading. |  |  |  |  |  |
|  | Multiply the reading of watt meter with 3 to get the total power of load. |  |  |  |  |  |
|  | Connect current coil of 1st watt meter in series to 1st phase and load. |  |  |  |  |  |
|  | Connect voltage coil of 1st watt meter to 1st phase and 3rd phase. |  |  |  |  |  |
|  | Connect current coil of 2nd watt meter in series to 2nd phase and load. |  |  |  |  |  |
|  | Connect voltage coil of 2nd watt meter to 2nd phase and 3rd phase. |  |  |  |  |  |
|  | Give supply and take the readings of both watt meter |  |  |  |  |  |
|  | Calculate the total power of load by adding the reading of both watt meter. |  |  |  |  |  |
|  | Connect phase line of AC supply to the left side terminal of energy meter. |  |  |  |  |  |
|  | Connect neutral line of AC supply to the next input terminal of energy meter. |  |  |  |  |  |
|  | Connect any AC load to the output terminals of energy meter. |  |  |  |  |  |
|  | Give supply and take reading of energy in terms of unit after few minutes form display. |  |  |  |  |  |
|  | Connect voltmeter & ampere meter with inductive load (Motor) |  |  |  |  |  |
|  | Connect watt meter with the load also. |  |  |  |  |  |
|  | Give AC supply and take the readings of volt, ampere and watt meter. |  |  |  |  |  |
|  | Utilize the above readings and calculate power factor using power formula P=VI |  |  |  |  |  |
|  | Connect current coil of power factor meter in series to the load. |  |  |  |  |  |
|  | Voltage coil of power factor meter in parallel to the load. |  |  |  |  |  |
|  | Give supply and note the value of power factor from power factor meter. |  |  |  |  |  |
|  | Connect ampere meter as well as current coil of power factor meter in series with load |  |  |  |  |  |
|  | Connect voltage coil of power factor meter in parallel to the load. |  |  |  |  |  |
|  | Connect a capacitor bank parallel to load. |  |  |  |  |  |
|  | Select the small value capacitor with the help of selector switch and give supply and note the value of power factor form power factor meter and current reading form ampere meter. |  |  |  |  |  |
|  | Now select the higher value of capacitor from capacitor bank with the help of selector switch and note its effect on power factor and load current. |  |  |  |  |  |
|  | Connect three phase supply with safety switch. |  |  |  |  |  |
|  | Connect all three leads of phase sequence meter with safety switch. |  |  |  |  |  |
|  | Push the button, and observe the direction of small induction motor, which is built-in in equipment. |  |  |  |  |  |
|  | If motor disc is rotating toward red mark clock wise, then phase sequence is correct. |  |  |  |  |  |
|  | Opposite direction will indicate the wrong phase sequence. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | National Diploma Level-5 in Telecommunication Technology Basic Electrical Engineering |
| --- | --- |
| Competency Standard(s) | Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence |
| Candidate Details | Name:_______________________________________________________________________ Registration/Roll Number: __________________ Candidate Signature:__________________ |
| Assessment Outcome | COMPETENT NOT YET COMPETENT Name of the Assessor:__________________________ Assessor’s code:_________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | What is the formula of D.C power? |  |  |
|  | How can we measure power of any circuit directly with any meter? |  |  |
|  | What is difference between electrical and mechanical power? |  |  |
|  | What is C.C (current coil)? |  |  |
|  | What is P.C (potential coil)? |  |  |
|  | What is three phase system? |  |  |
|  | What is wattmeter? |  |  |
|  | What is balanced load? |  |  |
|  | What is the relationship between the individual wattmeter readings and the total three phase power? |  |  |
|  | Why do we use three wattmeter methods to measure three phase load? |  |  |
|  | What are advantages of three wattmeter method? |  |  |
|  | How can we connect three-watt meter for measurement of power in delta connection? |  |  |
|  | What is diffrence between power & Energy? |  |  |
|  | What is Revolution of Disk in energymeter? |  |  |
|  | What is loading Rheostat? |  |  |
|  | What is power factor? |  |  |
|  | What are the reasons of power factor lagging? |  |  |
|  | What is leading power factor? |  |  |
|  | How can we improve power factor of an A.C inductive circuit with capacitor? |  |  |
|  | What will be the effect of improved power factor on load Current? |  |  |
|  | What is phase sequence? |  |  |
|  | If the phase sequence of three phase motor is not correct, then what will happen with motor? |  |  |
|  | Why we indicate each phase by red yellow blue? |  |  |
|  | What is inductive load? |  |  |

Feedback to the Candidate

Candidate’s Signature________________________ Assessor’s Signature __________________

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | National Diploma Level-5 in Telecommunication Technology Basic Electrical Engineering |
| Competency Standards | Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence |
| Assessment Task | - Measure single phase power using Volt-Ampere meter method |
|  | - Measure single power using watt meter |
|  | - Measure 3 phase power with watt meter |
|  | - Measure power with two-watt meters |
|  | - Measure power with three-watt meters |
|  | - Measure consumed energy with Energy meter |
|  | - Measure power factor with voltmeter, ampere meter and watt meter |
|  | - Measure power factor with power factor meter |
|  | - Improve power factor & measure it with power factor meter |
|  | - Determine phase sequence with phase sequence meter |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Select a proper load to calculate the power and give supply to it. |  |  |
| - Measure the voltage and current by using voltmeter and ampere meter. |  |  |
| - Find power using power formula. |  |  |
| - Select a proper load to calculate the power and connect watt meter with it. |  |  |
| - Give supply and measure the reading of power. |  |  |
| - Connect current coil of watt meter in series to any phase and one terminal of balance load. |  |  |
| - Connect voltage coil of watt meter to that phase and neutral |  |  |
| - Give 3-phase supply to load and take reading. |  |  |
| - Multiply the reading of watt meter with 3 to get the total power of load. |  |  |
| - Connect current coil of 1st watt meter in series to 1st phase and load. |  |  |
| - Connect voltage coil of 1st watt meter to 1st phase and 3rd phase. |  |  |
| - Connect current coil of 2nd watt meter in series to 2nd phase and load. |  |  |
| - Connect voltage coil of 2nd watt meter to 2nd phase and 3rd phase. |  |  |
| - Give supply and take the readings of both watt meter |  |  |
| - Calculate the total power of load by adding the reading of both watt meter. |  |  |
| - Connect phase line of AC supply to the left side terminal of energy meter. |  |  |
| - Connect neutral line of AC supply to the next input terminal of energy meter. |  |  |
| - Connect any AC load to the output terminals of energy meter. |  |  |
| - Give supply and take reading of energy in terms of unit after few minutes form display. |  |  |
| - Connect voltmeter & ampere meter with inductive load (Motor) |  |  |
| - Connect watt meter with the load also. |  |  |
| - Give AC supply and take the readings of volt, ampere and watt meter. |  |  |
| - Utilize the above readings and calculate power factor using power formula P=VI |  |  |
| - Connect current coil of power factor meter in series to the load. |  |  |
| - Voltage coil of power factor meter in parallel to the load. |  |  |
| - Give supply and note the value of power factor from power factor meter. |  |  |
| - Connect ampere meter as well as current coil of power factor meter in series with load |  |  |
| - Connect voltage coil of power factor meter in parallel to the load. |  |  |
| - Connect a capacitor bank parallel to load. |  |  |
| - Select the small value capacitor with the help of selector switch and give supply and note the value of power factor form power factor meter and current reading form ampere meter. |  |  |
| - Now select the higher value of capacitor from capacitor bank with the help of selector switch and note its effect on power factor and load current. |  |  |
| - Connect three phase supply with safety switch. |  |  |
| - Connect all three leads of phase sequence meter with safety switch. |  |  |
| - Push the button, and observe the direction of small induction motor, which is built-in in equipment. |  |  |
| - Observe motor disc rotation clockwise/anti clockwise to ensure correct phase sequence. |  |  |

Candidate’s Signature___________________		Assessor’s Signature_____________________

Date: ________________________________

Instruction Sheet for the Candidate

| Qualification | National Diploma Level-5 in Telecommunication Technology Basic Electrical Engineering |
| --- | --- |
| Competency Standard(s) | Measure Electrical Power, Energy, Power Factor & Determine Phase Sequence |
| Purpose of Assessment | Formative Assessment |

| Candidate Details | Name__________________________________________________ Registration/Roll Number_____________________________________________ |
| --- | --- |
| Guidance for Candidate | To meet this standard you are required to complete the following within the given time frame (for practical demonstration & assessment): - Measure single phase power using Volt-Ampere meter method - Measure single power using watt meter - Measure 3 phase power with watt meter - Measure power with two-watt meters - Measure power with three-watt meters - Measure consumed energy with Energy meter - Measure power factor with voltmeter, ampere meter and watt meter - Measure power factor with power factor meter - Improve power factor & measure it with power factor meter - Determine phase sequence with phase sequence meter |
| Time: 7 hours | During a practical assessment, under observation by an assessor, you are required to 1. Measure single phase power using Volt-Ampere meter method - Select a proper load to calculate the power and give supply to it. - Measure the voltage and current by using voltmeter and ampere meter. - Find power using power formula. - Measure single power using watt meter - Select a proper load to calculate the power and connect watt meter with it. - Give supply and measure the reading of power. - Measure 3 phase power with watt meter - Connect current coil of watt meter in series to any phase and one terminal of balance load. - Connect voltage coil of watt meter to that phase and neutral - Give 3-phase supply to load and take reading. - Multiply the reading of watt meter with 3 to get the total power of load. - Measure power with two-watt meters - Connect current coil of 1st watt meter in series to 1st phase and load. - Connect voltage coil of 1st watt meter to 1st phase and 3rd phase. - Connect current coil of 2nd watt meter in series to 2nd phase and load. - Connect voltage coil of 2nd watt meter to 2nd phase and 3rd phase. - Give supply and take the readings of both watt meter - Calculate the total power of load by adding the reading of both watt meter. - Measure power with three-watt meters - Connect current coil of 1st watt meter in series to 1st phase and load. - Connect voltage coil of 1st watt meter to 1st phase and neutral. - Connect current coil of 2nd watt meter in series to 2nd phase and load. - Connect voltage coil of 2nd watt meter to 2nd phase and 3rd phase. - Give the supply and take the readings of both watt meter - Calculate the total power of load by adding the reading of both watt meter. - Measure consumed energy with Energy meter - Connect phase line of AC supply to the left side terminal of energy meter. - Connect neutral line of AC supply to the next input terminal of energy meter. - Connect any AC load to the output terminals of energy meter. - Give supply and take reading of energy in terms of unit after few minutes form display. - Measure power factor with voltmeter, ampere meter and watt meter - Connect voltmeter & ampere meter with inductive load (Motor) - Connect watt meter with the load also. - Give AC supply and take the readings of volt, ampere and watt meter. - Utilize the above readings and calculate power factor using power formula P=VI - Measure power factor with power factor meter - Connect current coil of power factor meter in series to the load. - Voltage coil of power factor meter in parallel to the load. - Give supply and note the value of power factor from power factor meter. - Improve power factor & measure it with power factor meter - Connect ampere meter as well as current coil of power factor meter in series with load - Connect voltage coil of power factor meter in parallel to the load. - Connect a capacitor bank parallel to load. - Select the small value capacitor with the help of selector switch and give supply and note the value of power factor form power factor meter and current reading form ampere meter. - Now select the higher value of capacitor form capacitor bank with the help of selector switch and note its effect on power factor and load current. - Determine phase sequence with phase sequence meter - Connect three phase supply with safety switch. - Connect all three leads of phase sequence meter with safety switch. - Push the button, and observe the direction of small induction motor, which is built-in in equipment. - If motor disc is rotating toward red mark clock wise, then phase sequence is correct. - Opposite direction will indicate the wrong phase sequence. |
| Minimum Evidence Required |  |