Assessors Judgment Guide

| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Power Plant Technician (Telecom) Level-5 |
| --- | --- |
| Competency Standard(s) | 0714-E&A-37: Install and maintain Diesel Generator,solar power System,earthing, lightening arrester |
| Candidate Details | Name:_______ _______________________________________ Registration/Roll Number: ________________________Signature: ____________________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor________________________ Assessor’s code:___________________ Signature:__________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | Perform following tasks - Trouble Shooting of Diesel Generator Faults of Telecom System - Install Solar Power System for Telecom System - Construct Grounding/Earthling System for Telecom System - Install Lightening Arrester for Telecom System |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Trouble Shooting of Diesel Generator Faults of Telecom System |  |  |  |  |  |
|  | Identify the possible faults in DG. |  |  |  |  |  |
|  | Rectify auto starting issue by checking Fuel Level, Engine Oil Level, Heat alarm and inspect Radiator of DG. |  |  |  |  |  |
|  | Perform required action to rectify the above mention faults. |  |  |  |  |  |
|  | Rectify the fault DG starts automatically main AC supply is also available. |  |  |  |  |  |
|  | Measure the AC input voltage .in case of low voltage and any phase missing this fault occur. |  |  |  |  |  |
|  | Rectify the above mention reasons. |  |  |  |  |  |
|  | Rectify common faults like Weak battery, Self-fault. Loose connection in ATS. Low RPM. |  |  |  |  |  |
|  | Install Solar Power System for Telecom System |  |  |  |  |  |
|  | Install/Mount Solar Panels racks at Roof at a suitable place |  |  |  |  |  |
|  | Fixed the solar panels on racks/stands. |  |  |  |  |  |
|  | Install charge controller at a specified place. |  |  |  |  |  |
|  | Lay the cables for connection of charge controller, panels and batteries. |  |  |  |  |  |
|  | Connect solar panels with charge controller and charge controller with Batteries |  |  |  |  |  |
|  | Construct Grounding/Earthling System for Telecom System |  |  |  |  |  |
|  | Excavate/ dig a 5x5ft (1.5×1.5m) pit about 20-30ft (6-9 meters) in the ground. (Note that, depth and width depend on the nature and structure of the ground) |  |  |  |  |  |
|  | Bury an appropriate (usually 2’ x 2’ x 1/8” (600x600x300 mm) copper plate in that pit in vertical position. |  |  |  |  |  |
|  | Tight earth lead through nut bolts from two different places on earth plate. |  |  |  |  |  |
|  | Connect two earth leads with each earth plate (in case of two earth plates) and tight them. |  |  |  |  |  |
|  | Put grease around joints to protect from corrosion. |  |  |  |  |  |
|  | Collect all the wires in a metallic pipe from the earth electrode(s). Make sure the pipe is 1ft (30cm) above the surface of the ground. |  |  |  |  |  |
|  | Fill 1ft (30cm) layer of powdered charcoal (powdered wood coal) and lime mixture around the earth plate of around the earth plate. |  |  |  |  |  |
|  | Connect telecom system by using thimble and nut bolts to connect tightly wires to the system. Each system should be earthed from two different places. The minimum distance between two earth electrodes should be 10 ft. (3m). |  |  |  |  |  |
|  | Conduct Earth continuity test. |  |  |  |  |  |
|  | Test the overall earthing system through earth tester. If everything is going about the planning, then fill the pit with soil. The maximum allowable resistance for Earthing is 1Ω. Earth resistance without load (up to 1 Ohm) and with Load (up to 3 to 5 Ohm). |  |  |  |  |  |
|  | Install Lightening Arrester for Telecom System |  |  |  |  |  |
|  | Install/Mount Lightening Arrester rod on top of the Telecom Tower, System. |  |  |  |  |  |
|  | Connect and lay the cable from Lightening arrester to Down converter system and system earth point. |  |  |  |  |  |
|  | Connect Lightening arrester to earth point. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Power Plant Technician (Telecom) Level-5 |
| --- | --- |
| Competency Standard(s) | Install and maintain Diesel Generator,solar power System,earthing, lightening arrester |
| Candidate Details | Name:_______________________________________________________________________ Registration/Roll Number: __________________ Candidate Signature:__________________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor:__________________________Assessor’s code:_________________ Signature of the Assessor:_______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | Input and output voltage levels. |  |  |
|  | Line regulation and load regulation |  |  |
|  | Rectifier working. |  |  |
|  | rectifier input and output power connections. |  |  |
|  | SPD connection with rectifier. |  |  |
|  | Commissioning of rectifier system. |  |  |
|  | Battery resistance/conductance/impedance. |  |  |
|  | Battery without load and on load test |  |  |

Feedback to the Candidate

Candidate’s Signature________________________ Assessor’s Signature _________________________

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Power Plant Technician (Telecom) Level-5 |
| Competency Standards | Install and maintain Diesel Generator,solar power System,earthing, lightening arrester |
| Assessment Task | - Trouble Shooting of Diesel Generator Faults of Telecom System - Install Solar Power System for Telecom System - Construct Grounding/Earthling System for Telecom System - Install Lightening Arrester for Telecom System |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| Trouble Shooting of Diesel Generator Faults of Telecom System |  |  |
| Identify the possible faults in DG. |  |  |
| Rectify auto starting issue by checking Fuel Level, Engine Oil Level, Heat alarm and inspect Radiator of DG. |  |  |
| Perform required action to rectify the above mention faults. |  |  |
| Rectify the fault DG starts automatically main AC supply is also available. |  |  |
| Measure the AC input voltage .in case of low voltage and any phase missing this fault occur. |  |  |
| Rectify the above mention reasons. |  |  |
| Rectify common faults like Weak battery, Self-fault. Loose connection in ATS. Low RPM. |  |  |
| Install Solar Power System for Telecom System |  |  |
| Install/Mount Solar Panels racks at Roof at a suitable place |  |  |
| Fixed the solar panels on racks/stands. |  |  |
| Install charge controller at a specified place. |  |  |
| Lay the cables for connection of charge controller, panels and batteries. |  |  |
| Connect solar panels with charge controller and charge controller with Batteries |  |  |
| Construct Grounding/Earthling System for Telecom System |  |  |
| Excavate/ dig a 5x5ft (1.5×1.5m) pit about 20-30ft (6-9 meters) in the ground. (Note that, depth and width depend on the nature and structure of the ground) |  |  |
| Bury an appropriate (usually 2’ x 2’ x 1/8” (600x600x300 mm) copper plate in that pit in vertical position. |  |  |
| Tight earth lead through nut bolts from two different places on earth plate. |  |  |
| Connect two earth leads with each earth plate (in case of two earth plates) and tight them. |  |  |
| Put grease around joints to protect from corrosion. |  |  |
| Collect all the wires in a metallic pipe from the earth electrode(s). Make sure the pipe is 1ft (30cm) above the surface of the ground. |  |  |
| Fill 1ft (30cm) layer of powdered charcoal (powdered wood coal) and lime mixture around the earth plate of around the earth plate. |  |  |
| Connect telecom system by using thimble and nut bolts to connect tightly wires to the system. Each system should be earthed from two different places. The minimum distance between two earth electrodes should be 10 ft. (3m). |  |  |
| Conduct Earth continuity test. |  |  |
| Test the overall earthing system through earth tester. If everything is going about the planning, then fill the pit with soil. The maximum allowable resistance for Earthing is 1Ω. Earth resistance without load (up to 1 Ohm) and with Load (up to 3 to 5 Ohm). |  |  |
| Install Lightening Arrester for Telecom System |  |  |
| Install/Mount Lightening Arrester rod on top of the Telecom Tower, System. |  |  |
| Connect and lay the cable from Lightening arrester to Down converter system and system earth point. |  |  |
| Connect Lightening arrester to earth point. |  |  |

Candidate’s Signature___________________		Assessor’s Signature_____________________

Date: ________________________________

Instruction Sheet for the Candidate

| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Power Plant Technician (Telecom) Level-5 |
| --- | --- |
| Competency Standard(s) | Install Power Plant System |
| Purpose of Assessment | Formative assesment |

| Candidate Details | Name________________________________________________________ Registration/Roll Number_____________________________________________ |
| --- | --- |
| Guidance for Candidate | To meet this standard, you are required to complete the following within the 5 Hours (for practical demonstration & assessment): - Trouble Shooting of Diesel Generator Faults of Telecom System - Install Solar Power System for Telecom System - Construct Grounding/Earthling System for Telecom System - Install Lightening Arrester for Telecom System |
| Time: 5 Hours | During a practical assessment, under observation by an assessor, you are required to - Trouble Shooting of Diesel Generator Faults of Telecom System - Identify the possible faults in DG. - Rectify auto starting issue by checking Fuel Level, Engine Oil Level, Heat alarm and inspect Radiator of DG. - Perform required action to rectify the above mention faults. - Rectify the fault DG starts automatically main AC supply is also available. - Measure the AC input voltage .in case of low voltage and any phase missing this fault occur. - Rectify the above mention reasons. - Rectify common faults like Weak battery, Self-fault. Loose connection in ATS. Low RPM - Install Solar Power System for Telecom System - Install/Mount Solar Panels racks at Roof at a suitable place - Fixed the solar panels on racks/stands. - Install charge controller at a specified place. - Lay the cables for connection of charge controller, panels and batteries. - Connect solar panels with charge controller and charge controller with Batteries. - Construct Grounding/Earthling System for Telecom System - Excavate/ dig a 5x5ft (1.5×1.5m) pit about 20-30ft (6-9 meters) in the ground. (Note that, depth and width depend on the nature and structure of the ground) - Bury an appropriate (usually 2’ x 2’ x 1/8” (600x600x300 mm) copper plate in that pit in vertical position. - Tight earth lead through nut bolts from two different places on earth plate. - Connect two earth leads with each earth plate (in case of two earth plates) and tight them. - Put grease around joints to protect from corrosion. - Collect all the wires in a metallic pipe from the earth electrode(s). Make sure the pipe is 1ft (30cm) above the surface of the ground. - Fill 1ft (30cm) layer of powdered charcoal (powdered wood coal) and lime mixture around the earth plate of around the earth plate. - Connect telecom system by using thimble and nut bolts to connect tightly wires to the system. Each system should be earthed from two different places. The minimum distance between two earth electrodes should be 10 ft. (3m). - Conduct Earth continuity test. - Test the overall earthing system through earth tester. If everything is going about the planning, then fill the pit with soil. The maximum allowable resistance for Earthing is 1Ω. Earth resistance without load (up to 1 Ohm) and with Load (up to 3 to 5 Ohm). Install Lightening Arrester for Telecom System - Install/Mount Lightening Arrester rod on top of the Telecom Tower, System. - P2. Connect and lay the cable from Lightening arrester to Down converter system and system earth point. - P3. Connect Lightening arrester to earth point. |
| Minimum Evidence Required |  |

| Tools and Equipment |  |
| --- | --- |
| - Trainer - Multi meter - Connecting wire. - Transformers - Trainer - Connecting wire. - Battery lifting equipment - Full face shield. - Complete Tool kit of screws and wrenches. - Complete Electrical Toolkit - Torque wrench calibrated in inch-pounds, insulated. - Insulated Shoes | - Complete Electrical Tools kit. - Earth Tester. - Digging Equipment - RLC Meter - Digital Multi Meter - Digital Oscilloscope - Power Supply - Digital voltmeter. - Impedance Meter - Clamp Meter - Rubber gloves - Safety Helmet |