Instruction Sheet for the Candidate

| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Basic Electrical Wiring Level-5 |
| --- | --- |
| Competency Standard | 0714-E&A-90: Perform Testing of Electrical Wiring |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name______________________________________________________ Registration/Roll Number_______________________________________ |
| Guidance for Candidate | To meet this standard, you are required to complete the following within 04 Hrs. Time frame (for practical demonstration & assessment): |
| Time: 04 Hrs. | During a practical assessment, under observation by an assessor, you are required to - Perform Earth leakage Test. - Perform Open Circuit Test - Perform Short Circuit Test - Perform Continuity/Loop Test - Perform Visual Test - Perform Insulation Test - Perform Polarity Test - Perform Earth Resistance Test - Perform Murray Loop Test - Perform BLAVIER & Earth Loop Test |
| Minimum Evidence Required | - Perform Earth leakage Test. - Ensure the socket must be at least 13A for RCD plug in. - Adjust the sensitivity of RCD. - Ensure tripping time must not exceed than 200msec. - Plug the RCD in socket and switch on socket outlet. - Ensure P-N and P-E light up. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move the selection switch to 180o. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move selection switch to 00. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Perform Open Circuit Test - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect ohmmeter between starting and ending terminals of live conductor. - Ensure the reading must be near to 0 ohm. - Repeat P2 to P3 for neutral and earth conductor. - Perform Short Circuit Test - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect one terminal of ohmmeter with live conductor. - Connect the other terminals of ohmmeter with neutral conductor. - Ensure the reading must be infinity (No reading). - Connect ohmmeter between live conductor and earth conductor. - Ensure the reading must be infinity (No reading) - Perform Continuity/Loop Test - Connect all metal clad switches, metal parts, conduits with earth. - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent earth. - Measure the resistance value with tester which must not be more than 1 ohm. - Perform Visual Test - Check the wires joints. - Check if there is any spark. - Check over heating of wires. - Check all the appliances are on or fluctuating. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. - Perform Insulation Test - Switch off the main breaker. - Short circuit all lighting connections. - Connect merger between line and earth. - Rotate the merger to generate the voltage. - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. - Perform Polarity Test - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect ohm meter between main line and all the terminal of sockets and load points one by one. - Ensure meter reading value must be less than 1 ohm. - Perform Earth Resistance Test - Place 3 electrodes in earth at distance of 10m apart between every electrode. - Connect terminal E of earth resistance tester to first electrode. - Connect terminal P of earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat P1 to P5 by interacting earthling regions. - Ensure 3 readings must be equal. Perform Murray Loop Test - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. - Perform BLAVIER & Earth Loop Test - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. |

Self-Assessment Checklist

| Candidate Name |  |
| --- | --- |
| Registration No. |  |
| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Basic Electrical Wiring Level-5 |
| Competency Standard | Perform Testing of Electrical Wiring |
| Purpose of Assessment | Formative Assessment |
| Assessment Task | 1. Perform Earth leakage Test. 2. Perform Open Circuit Test 3. Perform Short Circuit Test 4. Perform Continuity/Loop Test 5. Perform Visual Test 6. Perform Insulation Test 7. Perform Polarity Test 8. Perform Earth Resistance Test 9. Perform Murray Loop Test 10. Perform BLAVIER & Earth Loop Test |

I can……………….

| Performance Criteria | Yes | No |
| --- | --- | --- |
| - Ensure the socket must be at least 13A for RCD plug in. |  |  |
| - Adjust the sensitivity of RCD. |  |  |
| - Ensure tripping time must not exceed than 200msec. |  |  |
| - Plug the RCD in socket and switch on socket outlet. |  |  |
| - Ensure P-N and P-E light up. |  |  |
| - Press the test button. |  |  |
| - Ensure that RCD will trip and reading must be shown less than 200msec. |  |  |
| - Move the selection switch to 180o. |  |  |
| - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |
| - Connect ohmmeter between starting and ending terminals of live conductor. |  |  |
| - Ensure the reading must be near to 0 ohm. |  |  |
| - Repeat P2 to P3 for neutral and earth conductor. |  |  |
| - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |
| - Connect one terminal of ohmmeter with live conductor. |  |  |
| - Connect the other terminals of ohmmeter with neutral conductor. |  |  |
| - Ensure the reading must be infinity (No reading). |  |  |
| - Connect ohmmeter between live conductor and earth conductor. |  |  |
| - Connect all metal clad switches, metal parts, conduits with earth. |  |  |
| - Open the main switch. |  |  |
| - Turn on all the switches. |  |  |
| - Connect earth continuity tester with conduit and independent earth. |  |  |
| - Measure the resistance value with tester which must not be more than 1 ohm. |  |  |
| - Check the wires joints. |  |  |
| - Check if there is any spark. |  |  |
| - Check over heating of wires. |  |  |
| - Check all the appliances are on or fluctuating. |  |  |
| - Check all indications of meters. |  |  |
| - Check Voltages on all phases. |  |  |
| - Check the DB and Breakers. |  |  |
| - Check the main supply is coming properly. |  |  |
| - Switch off the main breaker. |  |  |
| - Short circuit all lighting connections. |  |  |
| - Connect merger between line and earth. |  |  |
| - Rotate the merger to generate the voltage. |  |  |
| - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. |  |  |
| - Disconnect all loads. |  |  |
| - Switch on all circuit control switches. |  |  |
| - Connect ohm meter between main line and all the terminal of sockets and load points one by one. |  |  |
| - Ensure meter reading value must be less than 1 ohm. |  |  |
| - Place 3 electrodes in earth at distance of 10m apart between every electrode. |  |  |
| - Connect terminal E of earth resistance tester to first electrode. |  |  |
| - Connect terminal P of earth resistance tester to the second electrode. |  |  |
| - Connect terminal C of the earth resistance tester with third electrode. |  |  |
| - Measure the resistances after applying specific voltage. |  |  |
| - Repeat P1 to P5 by interacting earthling regions. |  |  |
| - Ensure 3 readings must be equal. |  |  |
| - Connect galvanometer with Wheatstone bridge. |  |  |
| - Connect positive terminal of DC source with Wheatstone bridge. |  |  |
| - Connect negative terminal of DC source with ground. |  |  |
| - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |
| - Short the other end of these two cores of cable. |  |  |
| - Note the reading of galvanometer. |  |  |
| - Calculate Rx. |  |  |
| - Repeat the P1 to P7 for other cores of the cable. |  |  |

Candidate’s Signature__________________ Assessor’s Signature____________________

Date: _______________________________

Assessors Judgment Guide

| Qualification | National Diploma Level-5 in Telecommunication Technology National vocational certificate of Basic Electrical Wiring Level-5 |
| --- | --- |
| Competency Standard | Perform Testing of Electrical Wiring |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: ______________________Signature: _______________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor________________________________________________ Assessor’s code: ____________________________________________________ Signature: ________________________________ |

| Assessment Summary (to be filled by the assessor) |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Activity | Method |  |  |  |  | Result |  |
| Nature of Activity | Written | Oral | Observation | Portfolio | Role Play | Competent | Not Yet Competent |
| Practical Skill Demonstration |  |  |  |  |  |  |  |
| Knowledge Assessment |  |  |  |  |  |  |  |
| Other Requirement |  |  |  |  |  |  |  |

Observation Checklist

| Assessment Task |  | - Perform Earth leakage Test. |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | - Perform Open Circuit Test |  |  |  |  |
|  |  | - Perform Short Circuit Test |  |  |  |  |
|  |  | - Perform Continuity/Loop Test |  |  |  |  |
|  |  | - Perform Visual Test |  |  |  |  |
|  |  | - Perform Insulation Test |  |  |  |  |
|  |  | - Perform Polarity Test |  |  |  |  |
|  |  | - Perform Earth Resistance Test |  |  |  |  |
|  |  | - Perform Murray Loop Test |  |  |  |  |
|  |  | - Perform BLAVIER & Earth Loop Test |  |  |  |  |
| During the practical assessment, candidate demonstrated the following: |  |  |  | Yes | No | Remarks |
|  | Ensured the socket must be at least 13A for RCD plug in. |  |  |  |  |  |
|  | Adjusted the sensitivity of RCD. |  |  |  |  |  |
|  | Ensured tripping time must not exceed than 200msec. |  |  |  |  |  |
|  | Plugged the RCD in socket and switch on socket outlet. |  |  |  |  |  |
|  | Ensure P-N and P-E light up. |  |  |  |  |  |
|  | Pressed the test button. |  |  |  |  |  |
|  | Ensured that RCD will trip and reading must be shown less than 200msec. |  |  |  |  |  |
|  | Move the selection switch to 180o. |  |  |  |  |  |
|  | Disconnected the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connected ohmmeter between starting and ending terminals of live conductor. |  |  |  |  |  |
|  | Ensured the reading must be near to 0 ohm. |  |  |  |  |  |
|  | Repeated P2 to P3 for neutral and earth conductor. |  |  |  |  |  |
|  | Disconnected the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connected one terminal of ohmmeter with live conductor. |  |  |  |  |  |
|  | Connect the other terminals of ohmmeter with neutral conductor. |  |  |  |  |  |
|  | Ensured the reading must be infinity (No reading). |  |  |  |  |  |
|  | Connected ohmmeter between live conductor and earth conductor. |  |  |  |  |  |
|  | Connected all metal clad switches, metal parts, conduits with earth. |  |  |  |  |  |
|  | Opened the main switch. |  |  |  |  |  |
|  | Turned on all the switches. |  |  |  |  |  |
|  | Connected earth continuity tester with conduit and independent earth. |  |  |  |  |  |
|  | Measured the resistance value with tester which must not be more than 1 ohm. |  |  |  |  |  |
|  | Checked the wires joints. |  |  |  |  |  |
|  | Checked if there is any spark. |  |  |  |  |  |
|  | Checked over heating of wires. |  |  |  |  |  |
|  | Checked all the appliances are on or fluctuating. |  |  |  |  |  |
|  | Checked all indications of meters. |  |  |  |  |  |
|  | Checked Voltages on all phases. |  |  |  |  |  |
|  | Check the DB and Breakers. |  |  |  |  |  |
|  | Checked the main supply is coming properly. |  |  |  |  |  |
|  | Switched off the main breaker. |  |  |  |  |  |
|  | Shorted circuit all lighting connections. |  |  |  |  |  |
|  | Connected merger between line and earth. |  |  |  |  |  |
|  | Rotated the merger to generate the voltage. |  |  |  |  |  |
|  | Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. |  |  |  |  |  |
|  | Disconnected all loads. |  |  |  |  |  |
|  | Switched on all circuit control switches. |  |  |  |  |  |
|  | Connected ohm meter between main line and all the terminal of sockets and load points one by one. |  |  |  |  |  |
|  | Ensured meter reading value must be less than 1 ohm. |  |  |  |  |  |
|  | Placed 3 electrodes in earth at distance of 10m apart between every electrode. |  |  |  |  |  |
|  | Connect terminal E of earth resistance tester to first electrode. |  |  |  |  |  |
|  | Connected terminal P of earth resistance tester to the second electrode. |  |  |  |  |  |
|  | Connected terminal C of the earth resistance tester with third electrode. |  |  |  |  |  |
|  | Measured the resistances after applying specific voltage. |  |  |  |  |  |
|  | Repeated P1 to P5 by interacting earthling regions. |  |  |  |  |  |
|  | Ensured 3 readings must be equal. |  |  |  |  |  |
|  | Connected galvanometer with Wheatstone bridge. |  |  |  |  |  |
|  | Connected positive terminal of DC source with Wheatstone bridge. |  |  |  |  |  |
|  | Connected negative terminal of DC source with ground. |  |  |  |  |  |
|  | Connected remaining two terminal of Wheatstone bridge with two cores of the cable. |  |  |  |  |  |
|  | Shorted the other end of these two cores of cable. |  |  |  |  |  |
|  | Noted the reading of galvanometer. |  |  |  |  |  |
|  | Calculated Rx. |  |  |  |  |  |
|  | Repeated the P1 to P7 for other cores of the cable. |  |  |  |  |  |
|  | Ensured the socket must be at least 13A for RCD plug in. |  |  |  |  |  |
|  | Adjusted the sensitivity of RCD. |  |  |  |  |  |
|  | Ensured tripping time must not exceed than 200msec. |  |  |  |  |  |
|  | Plugged the RCD in socket and switch on socket outlet. |  |  |  |  |  |
|  | Ensured P-N and P-E light up. |  |  |  |  |  |
|  | Pressed the test button. |  |  |  |  |  |
|  | Ensured that RCD will trip and reading must be shown less than 200msec. |  |  |  |  |  |
|  | Move the selection switch to 180o. |  |  |  |  |  |
|  | Disconnected the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connected ohmmeter between starting and ending terminals of live conductor. |  |  |  |  |  |
|  | Ensured the reading must be near to 0 ohm. |  |  |  |  |  |
|  | Repeated P2 to P3 for neutral and earth conductor. |  |  |  |  |  |
|  | Disconnected the supply source, neutral conductor and earth conductor from distribution fuse box. |  |  |  |  |  |
|  | Connect one terminal of ohmmeter with live conductor. |  |  |  |  |  |
|  | Connected the other terminals of ohmmeter with neutral conductor. |  |  |  |  |  |
|  | Ensured the reading must be infinity (No reading). |  |  |  |  |  |
|  | Connected ohmmeter between live conductor and earth conductor. |  |  |  |  |  |
|  | Connected all metal clad switches, metal parts, conduits with earth. |  |  |  |  |  |
|  | Opened the main switch. |  |  |  |  |  |
|  | Turned on all the switches. |  |  |  |  |  |
| Competent |  |  | Not Yet Competent |  |  |  |

Knowledge Assessment

| Qualification | National Diploma Level-5 in Telecommunication Technology Basic Electrical Wiring (Single Phase) |
| --- | --- |
| Competency Standard | Perform Testing of Electrical Wiring |
| Purpose of Assessment | Formative Assessment |
| Candidate Details | Name: ______________________________________________________________ Registration/Roll Number: _________________ Candidate Signature: ___________ |
| Assessment Outcome | COMPETENT NOT YETCOMPETENT Name of the Assessor: ________________________________________________ Assessor’s code: ____________________________________________________ Signature of the Assessor: _______________________ |

Candidate’s response is not required to be identical, but similar concepts and/or keywords must be used. Oral questioning may be used to clarify candidate understanding of topic and its application.

| Questions (Candidate confidently answered questions correctly and demonstrated understanding of the topics and their application) |  | Satisfactory | Not Satisfactory |
| --- | --- | --- | --- |
|  | Define RCD |  |  |
|  | Define sensitivity |  |  |
|  | Explain the purpose of Murray loop test. |  |  |
|  | Describe why Wheatstone bridge is attached in Murray loop test. |  |  |
|  | Define current, voltage, power and resistance. |  |  |
|  | Explain the purpose of Galvanometer. |  |  |
| 10 |  |  |  |
| 11 |  |  |  |

Feedback to the Candidate

Candidate’s Signature__________________ Assessor’s Signature _________________