National Vocational Certificate Level-3 in “Water Quality and Resource Management” (Water Quality Surveyor)

National Vocational and Technical Training Commission (NAVTTC),

Government of Pakistan

ACKNOWLEDGEMENT

National Vocational and Technical Training Commission (NAVTTC) extends its gratitude and appreciation to many representatives of business, industry, academia, government organizations, Provincial TEVTAs, Sector Skill Councils and trade associations who speared their time and expertise to the development and validation of these National Vocational Qualifications (Competency Standards, Curricula, Assessments Packs and related material). This work would not have been possible without the financial and technical support of the TVET Sector Support Program (TSSP)co-funded by European Union, Norwegian and German Governments implemented by GIZ Pakistan. NAVTTC is especially indebted to Dr. Muqeem ul Islam, who led the project from the front. The core team was comprised on:

- Dr. Muqeem ul Islam, Director General (Skills, Standards and Curricula) NAVTTC

- Mr. Muhammad Naeem Akhtar, Senior Technical Advisor TSSP-GIZ,

- Mr. Muhammad Yasir, Deputy Director (SS&C Wing) NAVTTC

- Mr. Muhammad Ishaq, Deputy Director (SS&C Wing) NAVTTC

- Mr. Muhammad Fayyaz Soomro, Deputy Director (SS&C Wing) NAVTTC

NAVTTC team under the leadership of Dr. Muqeem ul Islam initiated development of CBT & A based qualifications of diploma level-5 as a reform project of TVET sector in November 2018 and completed 27 NVQF diplomas of Level-5 in September, 2019. It seems worth highlighting that during this endeavor apart from developing competency standards/curricula in conventional trades new dimensions containing high-tech trades in TVET sector in the context of generation IR 4.0 trades have also been developed which inter alia includes Robotics, Mechatronics, artificial intelligence, industrial automation, instrumentation and process control. Moreover, trades like entrepreneurship, green/environmental skills and variety of soft/digital skill have also been developed to equip the Pakistani youth with skills set as per requirement of the global trends. These skills have been made integral part of all the 27 diplomas.

Nobody has been more important in the pursuit of this project than Dr. Nasir Khan, Executive Director, NAVTTC, whose patronage and support remain there throughout the development process and lastly to thanks especially to Syed Javed Hassan, Chairman NAVTTC and Raja Saad Khan, Deputy Team Lead TSSP-GIZ who made it happened in this challenging time.

- Table of Contents

1.	Introduction	6

2.	Purpose of the Qualification	6

3.	Date of Validation	6

4.	Date of Review	6

5.	Codes of Qualifications	7

6.	Members of Qualification Development Committee	8

7.	Members of Qualification Validation Committee	9

8.	Entry Requirements	10

9. Summary and Leveling of Competency Standards	10

Demonstrate the regulatory requirements for water and wastewater quality	11

Identify the requirements of national policies on water and environment	11

9.	Detail of Qualification and its Competency Standards	13

1.	Water and waste water sampling and field monitoring	13

1021CS-01.	Perform Pre Sampling Operations	13

1021CS-02.	Perform Sampling (Ground Water Collection)	16

1021CS-03.	Perform Water Quality Sampling (Surface Water)	18

1021CS-04.	Collect Water Quality Samples for Quality Control	21

1021CS-05.	Perform on site Field Testing	22

1021CS-06.	Store and transport the samples to laboratory	24

2.	Water Quality Standards and Guidelines	25

1021CS-07.	Apply permissible limits for data interpretation	25

1021CS-08.	Analyze the Water Policies and Legislations	26

3.	Water and waste water Testing (Physico-chemical Parameter)-1I	27

1021CS-09.	Perform Testing of pH by pH Meter	27

1021CS-010.	Testing of Electrical Conductivity (EC) by EC Meter	30

1021CS-011.	Testing of Turbidity by Turbidity Meter	32

1021CS-012.	Testing of Calcium & Magnesium by EDTA Titrimetric Method	35

1021CS-013.	Testing/Determination of Hardness by EDTA Titrimetric Method	38

1021CS-014.	Testing/Determination of Alkalinity by Titrimetric Method	41

4.	Water Quality Testing for Microbiological Contamination-I	44

1021CS-015.	Perform Testing for Total Coliforms and Fecal Coliforms (Method-I)	44

1021CS-016.	Perform Testing for Total Coliforms and Fecal Coliforms (Method-II)	49

5.	Plumbing	53

1021CS-017.	Identify plumbing Tools and Equipment	53

1021CS-018.	Perform cutting, threading & reaming	55

1021CS-019.	Make Water Connection	57

1021CS-020.	Layout for domestic water supply	59

1021CS-021.	Join pipes & fittings	61

1021CS-022.	Install plumbing fixtures	65

1021CS-023.	Install & repair water pumps	69

1021CS-024.	Install turbine pumps	72

1021CS-025.	Prepare sketches of aqueducts & water pipes	74

1021CS-026.	Plan Water Distribution System	77

- Introduction

Water quality and treatment is process that improves the quality of water to make it more acceptable for specific end-use. The end use may be drinking, industrial water supply, irrigation, recreation water or many other uses, including being safely returned to the environment. Water treatment removes contaminants and undesirable components, or reduces their concentration so that the water becomes fit for its desired end-use. This treatment is crucial to human health and allows humans to benefit from both drinking and irrigation use.

In fact, no sphere of life may be identified that does not include contribution of the water. Thus, the importance of this diploma may be determined according to its usefulness in our daily life. Therefore, industry expectations for skilled workforce are also dynamic which can only be managed through setting relevant competency standards in collaboration with the leading industries. Being cognizant of this fact, National Vocational & Technical Training Commission (NAVTTC) developed competency standards for Water Quality and Treatment Technology under National Vocational Qualifications Framework (NVQF). These competency standards have been developed by a Qualifications Development Committee (QDC) and validated by the Qualifications Validation Committee (QVC) having representation from the leading organizations of water sector (PCRWR, WASA, PCSIR, PHED etc.)in the country.

- Purpose of the Qualification

The purpose of these qualification is to set high professional standards for Water Quality and Resource Management. The specific objectives of developing these qualifications are as under:

- Improve the professional competence of the graduates

- Provide opportunities for recognition of skills attained through non-formal or informal pathways

- Improve the quality and effectiveness of training and assessment for water sector

- Enable the existing workforce to capacitate themselves in new water technologies

- Date of Validation

The level 5 of National DAE qualification on Water Quality and Resource Management has been validated by the Qualifications Development Committee (QDC) members on 10-12thJune, 2019and will remain valid for ten years i.e.12th June, 2029

- Date of Review

The level 5 of National DAE qualification on Water Quality and Resource Management has been validated by the Qualifications Development Committee (QDC) members on 10-12thJune, 2019and shall be reviewed after three years i.e. 12th June, 2022

- Codes of Qualifications

The International Standard Classification of Education (ISCED) is a framework for assembling, compiling and analyzing cross-nationally comparable statistics on education and training. ISCED codes for these qualifications are assigned as follows:

| ISCED Classification |  |
| --- | --- |
| Code | Description |
| 1021CS (1) | National Vocational Certificate Level-I & II in “Water Quality and Resource Management” (Assistant) |
| 1021CS (2) | National Vocational Certificate Level-III in “Water Quality and Resource Management” (Water Quality Surveyor) |
| 1021CS (3) | National Vocational Certificate Level-IV in “Water Quality and Resource Management” (Lab Analyst) |
| 1021CS (4) | National Vocational Certificate Level-V in “Water Quality and Resource Management (Supervisor/ Water Treatment Technician) |

- Members of Qualification Development Committee

| S# | Name - Designation | Organization |
| --- | --- | --- |
|  | Ms. Lubna Naheed Bukhari | PRCWR, Islamabad |
|  | Dr. Hifza Rasheed, Director | PRCWR, Islamabad |
|  | Engr. Ahmed Shamsher, Deputy Secretary | PHED,KPK |
|  | Muhammad Adnan, Deputy Director | IMC, Islamabad |
|  | Dr. Asad Ghufran | IIUI, Islamabad |
|  | Mr. Azizullah Khan | WASA Rawalpindi |
|  | Dr. Anwer Baig | NUST |
|  | Miss Saiqa Imran | PRCWR, Islamabad |
|  | Mr. Shafiqur Rehman | PRCWR, Islamabad |
|  | Mr. Ali | PHED, Balochistan |
|  | Mr. Abdul Latif | PHED, Sindh |
|  | Mr. Tanveer Malik | Bin Qutab, Islamabad |
|  | Muhammad Yasir, Assistant Director | SS&C NAVTTC, Islamabad |
|  | Ms. Saba Sadiq, DACUM Facilitator | University of Lahore, Lahore |

- Members of Qualification Validation Committee

| S# | Name - Designation | Organization |
| --- | --- | --- |
|  | Dr.Muhammad Aslam Tahir, Chairman | PRCWR,Islamabad |
|  | Dr.Manzoor Ahmed Malik, Director | PRCWR,Islamabad |
|  | Engr.Faizan-ul-Hasan, Director | PRCWR,Islamabad |
|  | Dr.Hifza Rasheed, Director | PRCWR,Islamabad |
|  | Dr.Muhammad Arshad Malik, Assistant Professor | IIUI,Islamabad |
|  | Syed Musstajab Akbar Shah Eqani, Assistant Professor | COMSATS Islamabad |
|  | Engr.Ahmed Shamsher, Deputy Secretary | PHED,KPK |
|  | Muhammad Adnan, Deputy Director | IMC,Islamabad |
|  | Muhammad Zaheer, Assistant Director | NTB,Islamabad |
|  | Muhammad Yasir, Assistant Director | SS&C NAVTTC,Islamabad |
|  | Ms. Samreen Iqbal, Senior Scientist officer | Qarshi Industries, Islamabad |
|  | Ms. Saba Sadiq, DACUM Facilitator | University of Lahore, Lahore |

- Entry Requirements

The entry for National Vocational Certificate level 3, in Water Quality and Resource Management are

- A person having National Vocational Certificate level 1 & 2, in Water Quality and Resource Management

# 9. Summary and Leveling of Competency Standards

| National Vocational Certificate Level-3 in “Water Quality and Resource Management” (Water Quality Surveyor) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| NVQF (Competency Standards) | Level | Category | Estimated Hours |  |  | CH |  |
|  |  |  | Th. | Pr. | T H |  |  |
| Level 3 |  |  |  |  |  |  |  |
| 6. Water and Waste water Sampling and field Monitoring (Water Quality Surveyor) |  |  |  |  |  |  |  |
| Perform Pre Sampling Operations | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Perform Collection of Samples (Ground Water) | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Perform Water Quality Sampling (Surface Water) | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Collect Water Quality Samples for Quality Control | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Perform on site Field Testing | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Store and transport the samples to laboratory | 3 | Technical | 3 | 9 | 12 | 1.2 |  |
| Total |  |  | 18 | 54 | 72 | 7.2 |  |
| 7. Water Quality Standards and Guidelines |  |  |  |  |  |  |  |
| ## Demonstrate the regulatory requirements for water and wastewater quality | 3 | Technical | 10 | 20 | 30 | 3.0 |  |
| ## Identify the requirements of national policies on water and environment | 3 | Technical | 4 | 15 | 19 | 1.9 |  |
| Total |  |  | 14 | 35 | 49 | 4.9 |  |
| 8. Water and waste water Testing (Physico-chemical Parameter)-I |  |  |  |  |  |  |  |
| Perform Testing of pH by pH Meter | 3 | Technical | 6 | 14 | 20 | 2 |  |
| Perform Testing of Electrical Conductivity(EC) by EC Meter | 3 | Technical | 6 | 20 | 26 | 2.0 |  |
| Perform Testing of Turbidity by Turbidity Meter | 3 | Technical | 8 | 20 | 28 | 2.8 |  |
| Perform Testing of Calcium & Magnesium by EDTA Titrimetric Method | 3 | Technical | 10 | 35 | 45 | 4.5 |  |
| Perform Testing/Determination of Hardness by EDTA Titrimetric Method | 3 | Technical | 10 | 30 | 40 | 4.0 |  |
| Perform Testing/Determination of Alkalinity by Titrimetric Method | 3 | Technical | 10 | 30 | 40 | 4.0 |  |
| Total |  |  | 50 | 149 | 199 | 19.9 |  |
| 9. Water Quality Testing for Microbiological Contamination-I (Water Testing Technician (Microbiological) |  |  |  |  |  |  |  |
| Perform Testing for Total Coliforms and Fecal Coliforms (Method-I) | 3 | Technical | 18 | 35 | 53 | 5.3 |  |
| Perform Testing for Total Coliforms and Fecal Coliforms (Method-II) | 3 | Technical | 17 | 35 | 52 | 5.2 |  |
| Total |  |  | 35 | 70 | 105 | 10.5 |  |
| 10. Plumber |  |  |  |  |  |  |  |
| Identify plumbing tools & equipment | 3 | Technical | 5 | 10 | 15 | 1.5 |  |
| Perform cutting, threading & reaming | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Make water connection | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Layout for domestic water supply | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Install plumbing fixtures | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Install & repair water pumps | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Install turbine pumps | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Prepare sketches of aqueducts & water pipes | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Plan water distribution system | 3 | Technical | 5 | 15 | 20 | 2 |  |
| Total |  |  | 45 | 130 | 175 | 17.5 |  |
| Grand Total |  |  | 162 | 438 | 600 | 60 |  |

- Detail of Qualification and its Competency Standards

## Water and waste water sampling and field monitoring

### Perform Pre Sampling Operations

Overview: This competency standard covers the skill and knowledge required to demonstrate the Objectives of the Sampling, Prepare sampling plan and Identify Types of Water samples, preservatives, labeling and observe the site details.

| Competency Unit | Performance Criteria |
| --- | --- |
| - Demonstrate the Objectives of the Sampling | - Establish the scope and objectives of sampling as per project/assessment objectives. - Understand the purpose for which the various types of samples will be collected - Review site files and field folders. (Site location, description and access, and review any previously collected physical, chemical, and biological data.) - Decide sampling design and sample size - Fallow the standard methods for sampling |
| - Prepare Sampling Plan | - Plan field visits and formulate sampling team - Make checklist for pre-sampling, sampling and post sampling preparations - Select Suitable Sampling Techniques (Grab, composite) - Select Sampling Bottles and Preservatives as per requirements of water quality test parameters - Check calibrations of field equipment to perform Accurate Field Measurements - Check Maps, distance measuring equipment, global positioning systems, or other location determining equipment; |
| - Identify Types of Water samples, preservativesand labeling | - Type A – All sites –in sterilized 200 ml sampling bottles; fro microbiological analysis - Type B –All sites – with 2 ml/liter nitric acid as preservative for trace elements; - Type C –All sites – with 1 ml/100 ml, 1 M boric acid as preservative for nitrate; - Type D –All sites – no preservative for other water quality parameters; - Type E – Surface and drain water – in plastic bottles for COD and BOD; and - Type F – Surface water– in glass bottles for Persistent Organic Pollutants (POPs) - Label the sampling bottles with - The site code. - The parameter(s) to be measured. - The date of collection. - c. A unique sample number. |
| - Observe the Site Details | - Document all the information regarding location, depth, type, number of users, and anything unusual/notable around the sampling site/source. - Consider physical characteristics of the area, such as size and shape, land use, tributary and runoff characteristics, geology, - point and nonpoint sources of contamination, hydraulic conditions, climate, water depth for surface water sampling - Document Physical and meteorological conditions at time of sample collection. - Ensure Signatures or initials of appropriate field personnel. - Fill outperformat each site before moving to the next site. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Purpose of water Sampling

  - Procedure for Consistency and Representativeness of Sample

  - Prevention of Deterioration and Contamination

  - Location Selection

  - Relevant local area geography

  - Site details and other environmental factors

  - Weather conditions (temperature, wind, rainfall)

  - Presence of animals

  - Other comments (e.g. system problems i.e. disinfection/filtration equipment, fecal contamination)

Tools and Equipment

- Sampling checklist

- Field Testing Kits

- Map of the sites

- Polystyrene bottles of 0.5 and 1.5 liter capacities

- For bacterial analysis, samples were collected in pre sterilized bottles of 200 ml volume

- For analysis of trace elements and nitrate (nitrogen) nitric acid and boric acid respectively

- Water Sampling Questionnaire

- GPS

- Water Sampler

- Hand washer

- Protective equipment

- sample bottles

### Perform Sampling (Ground Water Collection)

Overview: This competency standard covers the skill and knowledge required to Collect sample for chemical analysis and Collect sample for Microbiological analysis.

| Competency Units | Performance Criteria |
| --- | --- |
| - Collect sample for chemical analysis | - Follow precautionary measures while collecting samples from the field. - Select an un-rusted tap while collecting water sample/s from water supply line/consumer end. - Clean the tap properly and allow to flow for a few minutes before collection of sample. - Collect the water sample from a tube well after allowing it to flow for at least 10 minutes to get representative sample of the groundwater. Record the depth of groundwater level. - Collect the water samples from a distribution network from the source of supply (tube well) as close as possible, to minimize the effects of pollution in the distribution system; and from consumer end (tap) to evaluate the actual quality of water being used. - Fill all the water sampling bottles slowly to avoid turbulence and air bubbles, after flushing the system for sufficient time. - Hand Pump/Dug Well: Collect the water sample from a selected hand pump or dug well after purging, making one stroke for every foot of depth (a hand pump or dug well having 30 feet of depth, needs 30 strokes for its purging). |
| - Collect sample for Microbiological analysis | - Collect the water samples for microbiological analysis in clean, sterile plastic bottles (200 ml). - Ensure that no accidental contamination occurs during sampling. - Take Samples from those taps, which were not leaking between the spindle and gland to avoid outside contamination. - Kept the samples cool (in ice box) and in dark during transportation to designated laboratory. Where there a proper place was available - Analyse the samples just after collection by field testing method. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Procedures and techniques and protection protocols for water sampling for chemical and biological contamination

  - Procedures for water sample preparation, including: prevention of contamination, volume of sample appropriate containers and preservation

  - Understand the Quality control procedures to estimate the Degree of Error due to Sampling, Preservation, and Transportation

Tools and Equipment

- Preservatives

- Sample bottles

- Permanent marker

### Perform Water Quality Sampling (Surface Water)

Overview:This competency standard covers the skill and knowledge required to Prepare work area, Direct Sampling and Grab Sampling.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare work area | - Determine the extent of the sampling effort, the sampling methods to be employed, equipment and supplies are needed. - Obtain necessary sampling and monitoring equipment. - Decontaminate or pre clean equipment, and ensure that it is in working order |
| - Take Direct Sample | - Ensure that labelling on the bottle to be filled is correct and that the sample number matches the number on the paperwork (field observation form). - Take the sample from the bank, or wade into the water in waders or boots, minimizing disturbance as much as possible. - Don’t uncap the bottle until just before the sample is to be taken. - When filling the bottle (both for rinsing and for the final sample) take the sample upstream and to the side of you. - Uncap the bottle to be filled, immerse the bottle in the water (to a depth of ~15cm) lying it flat with its mouth towards the flow of the water, then slowly move the bottle forwards into the flowing water. - If rinsing is required (make sure you check the standard operating procedure) allow approximately 20 mL of water to enter the bottle. Cap, shake well and pour the reinstate downstream of yourself. - Repeat twice so the bottle is rinsed a total of three times (if required). - Then fill the bottle, again upstream and to the side of yourself at a depth of~15 cm, moving it slowly forwards through the water to the required level (generally the shoulder of the bottle, but always check the sampling and analysis plan). Cap, and store the sample container as required for transport to the laboratory. - If bottles contain preservatives (i.e. for metal analysis), they must not be rinsed and should be filled by decanting from another, rinsed bottle. |
| - Take Grab sample | - Ensure that labelling on bottle to be filled is correct and that the sample number matches the number on the paperwork (field observation form). - Check that the grab sampler is clean; this should be done at the completion of each day’s sampling, normally by simply rinsing in tap water. - Extend the grab sampler so that it will reach to the point that you wish to sample. - Carefully lower the grab sampler into the water with the mouth of the bottle facing upstream into the flow of water to a depth of ~15 cm. Keep the bottle moving forward into the flow of water while it is filling - Allow the bottle to partially fill, take it out of the water, swirl around, and tip out rinsate downstream of sampling site. - Repeat twice so that the grab sampler has been rinsed three times. - Then, fill the grab sampler at a depth of ~15 cm, with the mouth of the bottle facing upstream, slowly moving the bottle forward into the flow of water. - Use this sample to rinse the labelled sample container three times using the same procedure as for taking a direct sample. - Then, fill the rinsed, labelled sample container from the grab sample bottle. It may be necessary to refill the grab sample bottle to obtain enough water to fill the sample container. If this is necessary, recap the sample container between top-ups. Fill the sample container to the required level (generally the shoulder, but check the sampling and analysis plan, as this may vary). - Take care not to touch the opening of the sample container with any part of the grab pole bottle or your hands as this can easily introduce contaminants to the sample. - If the sample container contains a preservative, be careful when filling to prevent any splash back. - Cap (tightly) and store the sample container as required for transport to the laboratory. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Purpose of water Sampling

  - Procedure for Consistency and Representativeness of Sample

  - Prevention of Deterioration and Contamination

  - Location Selection

  - relevant local area geography

  - site details and other environmental factors

  - Weather conditions (temperature, wind, rainfall)

  - Presence of animals

  - Other comments (e.g. system problems i.e. disinfection/filtration equipment, fecal accidents)

Tools and Equipment

- Surface water sampler

- Auto sampler

- Sample collection bottles

- Sample bottle preservatives

- Grab Sampler

### Collect Water Quality Samples for Quality Control

Overview:This competency standard covers the skill and knowledge required to Prepare Field blank and Collect Replicate samples

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare Field blank | - Take, extra labelled, empty containers for field blanks - Take suitable preservative - Filled containers with distilled deionized - Closed The bottle and handle the contents same as real samples during transfer and storage - label the sample as QC sample |
| - Collect Replicate samples | - Take at least two but preferably three samples simultaneously - Select same site, date, time, depth, matrix and method to establish the reproducibility of sampling. - Label the sample as QC Sample |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Procedures for water sample preparation, including: prevention of contamination, volume of sample appropriate containers and preservation

  - Procedures for collecting, labelling, transporting and storing samples

  - Understand the Quality control procedures to estimate the Degree of Error due to Sampling, Preservation, Transportation

Tools and Equipment

- Deionized Water

### Perform on site Field Testing

Overview:This competency standard covers the skill and knowledge required toPerform Pre- field calibration of Equipment,PerformPh,Perform Electrical conductivity and Perform Testing of Dissolved Oxygen

| Competency Units | Performance Criteria |
| --- | --- |
| - Perform Pre- field calibration of Equipment’s | - Be familiar with the contents of the operating manual for that specific instrument - Calibration must be undertaken as per the instrument manufacturer’s instructions - Make sure that the calibrating standards have not been expired. - Perform calibration using standards in the range of values expected to be encountered in the field. - Perform and record calibration before the start of a field trip, and should be checked at the conclusion of each field trip. - Calibrate/standardize the instrument with the calibrating standards as per the manufacturer instruction. |
| - Perform Ph | - Immersed the electrodes are either in, or rinsed with, distilled water. Remove them from the water and blot dry. - Rinse the electrodes and a small beaker with a portion of the sample. - Pour sufficient of the sample into the small beaker to allow the tips of the electrodes to be immersed to a depth of about 2 cm. The electrodes should be at least 1 cm away from the sides and the bottom of the beaker. - Measure the temperature of the water sample and set the temperature adjustment dial accordingly (if the instrument does not have automatic temperature compensation). - Turn on the pH meter. - Read the pH of the water sample on the meter. - Raise the electrodes out of the sample. Remove the sample and discard it. - Rinse the electrodes and the beaker with distilled water, and blot the electrodes with soft tissue. - Replace the protective rubber cap on the tip. - Switch the meter off and pack it in its carrying case for transport. |
| - Perform Electrical conductivity | - Rinse the conductivity cell with at least three portions of the sample. - Immerse the conductivity cell containing the electrodes in a sufficient volume of the sample for the liquid level to be above the vent holes in the cell. There should be no air bubbles clinging to the electrodes and the cell should not be closer than 2 cm to the sides and bottom of the container. - Turn the meter on. Follow the manufacturer’s operating instructions and record the meter reading. - Turn the meter off and pack it and the electrode in the carrying case for transport. |
| - Perform Testing of Dissolved Oxygen | - Calibrate/standardize the instrument as per the manufacturer instruction - Rinse the electrode in a portion of the sample which is to be analyzed for dissolved oxygen. - Immerse the electrode in the water, ensuring a continuous flow of water past the membrane to obtain a steady response on the meter. - Record the meter reading and the temperature - Switch the meter off and pack it and the electrode in the carrying case for transport. |

Tools and Equipment

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Portable Electrical Conductivity Meter

  - Portable pH Meter

  - Portable Dissolve Oxygen (DO)

  - Meter

  - Calibrating standards

  - EC, pH standards

  - Ice box

### Store and transport the samples to laboratory

Overview:This competency standard covers the skill and knowledge required to Store the samples and Transport the sample to laboratory.

| Competency Units | Performance Criteria |
| --- | --- |
| - Store the samples | - Place the samples bottles in a box for transport to the laboratory. - Use insulated wooden or plastic boxes - Protect samples from sunlight, prevent the breakage of sample bottles, - Maintain the temperature of the box 4 °C - Use ice packs or coolants |
| - Transport the sample | - Co-ordinate with the laboratory personnel’s. - Ensure that the samples will be delivered with in standard holding time - Let the analyst know the no. of samples - Coordinate the time of arrival of the samples - Communicate the results of any measurements completed in the field. |

Tools and Equipment

- Ice box

- Sample container

## Water Quality Standards and Guidelines

### Apply permissible limits for data interpretation

Overview: This competency standard covers the skills and knowledge required to interprete degree of fitness of water for drinking, environment and irrigation.

| Competency Units | Performance Criteria |
| --- | --- |

| - Identify/analyse water standards | - Apply National water quality standards - Apply National environmental quality standards, - Compare data with USEPA water quality standards, - Compare data with WHO Drinking water guidelines, - Compare data with Surface water and irrigation water quality standards/permissible limits. |
| --- | --- |

| - Apply water quality standards and guidelines for interpretation | - Interpret the water quality of major cities in line with regulatory standards. - Generate technical report by applying water quality standards on the test data |
| --- | --- |

Knowledge and understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Up-to-date knowledge and enhanced capacity in adopting the water and wastewater quality standards and test data interpretation

Tools and Equipment

- Published standards and guidelines

- Water quality test data

### Analyze the Water Policies and Legislations

Overview: This competency standard covers the skills and knowledge required to develop monitoring and mitigation measures in accordance with water policies/regulations.

| Competency Units | Performance Criteria |
| --- | --- |
| - Analyzenational water policies | - Identify relevant guidelines from National Drinking-Water Policy 2009 - Identify relevant guidelines from National water policy 2018 |
| - Analyze water related measures in policies other than water policies | - Identify relevant guidelines from National Environmental Policy 2005, - Identify relevant National Sanitation Policy 2006 - Identify National Climate Change Policy |
| - Understand provincial water policies for water safety | - Identify relevant Provincial water policies and regulations - Compare provincial policies for water/wastewater quality improvement |
| - Develop Implementation Framework | - Identify and enlist the relevant line departments for water supply - Prepare preliminary report containing viable major points for implementation - Submit report to the supervisor for further action |

Knowledge and understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Up-to-date knowledge and enhanced capacityfor implementing the policy frameworks and regulatory measures

Tools and Equipment

- Published Approved national and provincial policies, acts/regulations

- SDGs Reporting Systems/Tools

## Water and waste water Testing (Physico-chemical Parameter)-1I

### Perform Testing of pH by pH Meter

Overview:This competency standard covers the skill and knowledge required to prepare samples for laboratorytesting, Prepare for laboratory testing, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of pH testing. - Maintain the Laboratory room temperature at 25 °C minutes. - Prepare pH buffer solution. - Identify appropriate test method, equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up pH meter and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of pH meter. Perform calibration if required. |
| - Perform tests on samples | - Turn on the instrument and give it 5 minutes warm up time and press the desired mode of measurement. - Rinse the electrode with deionized water and check the calibration by running known buffers of pH (4.00, 7.00, and/or 10.00). - Take 50 ml sample in a beaker, immerse the probe and stir it until instrument gives stable pH reading. - Analyze three replicates (3 readings per sample) - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| - Quality Control Checks | - pH meter is standardized by running known standard. - Method blank is analyzed after every 10 samples. - Laboratory Control samples of pH 7.05 analyzed with every batch of 10 samples. - check repeatability by re-analyzing a pre-analyzed sample once a day. - Daily quality control data is recorded in QC Data sheet- - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to the laboratory reporting section - Clear and restore work area. |
| - Adopt precautions during work | - Ensure before taking any measurement that meter has been calibrated. - If the probe has been left dry, condition it in pH (7) solution at least for one hour to reactivate it. - Submerge the probe in the sample to be tested while stirring it gently. - If the measurements of different samples are taken successively rinse the probe tip thoroughly to eliminate cross contamination, after clearing rinse the probe tip with some of the sample to be measured. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of electrometric pH measurement i.e. determination of activity of the hydrogen ions by potentiometric measurement using a standard hydrogen electrode and a reference electrode

- Identifying pH hazards in water samples

- Planning and organizing testing assignment

- Using appropriate testing equipment and personal protective clothing and equipment

- Understanding and applying procedures for testing

- Determining and reporting accurate and relevant pH results from testing

Tools and Equipment

- pH Meter

- pH buffers of pH 4, 7 & 10

- Deionized water

- Glass Beaker (A Class)

### Testing of Electrical Conductivity (EC) by EC Meter

Overview:This competency standard covers the skill and knowledge required to prepare samples forlaboratorytesting, perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| CU1:Prepare samples for testing | - Check the sample label for the requirement of EC testing. - Maintain the Laboratory room temperature at 25 °C - keeps the sample at room temperature for few minutes. - Check for the availability of EC standard of concentration 1413 µS/cm. - Identify appropriate test method, equipment and safety requirements. |
| CU2:Prepare for laboratory testing | - Set up EC meter and/or reagents in accordance with the standard work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| CU3:Perform tests on samples | - Turn on the instrument and give it 5 minutes warm up time. Press the desired mode of measurement. - Rinse the electrode with deionized water and check the calibration by running known EC standard of concentration 1413 µS/cm. - Take 50 ml deionized water in a beaker, immerse the probe in it and stir the blank until the instrument gives stable EC reading. - Analyze three replicates (3 readings per sample) - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. |
| Cu4:Quality Control Checks | - Electrical Conductivity meter is standardized by running known standard. - Method blank is analyzed after every 10 samples. - Laboratory Control samples of 1413 µS/cm analyzed with every batch of 10 samples. - check repeatability by reanalyzing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| Cu5:.Record the results/ Finalize work | - Note down the results on analyst workbook. - Calculate uncertainty of the results. - Record the results on result record form and submit to the laboratory reporting section - Clear and restore work area. |
| CU 6 Adopt precautions during work | - Before taking any measurement makes sure the meter has been calibrated. - Warm up instrument for 5 minutes before start working on it. - Rinse its probe properly with deionized water and select desired mode of working. - The presence of particulate matter in the sample can lead to unstable and non-reproducible results. If necessary filter, or allow the particles to settle prior to immersion. - If the measurements of different samples are taken successively rinse the probe tip thoroughly to eliminate cross contamination, after clearing rinse the probe tip with some of the sample to be measured |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Demonstration of an ability to prepare water samples and perform quality tests according to specified standards and parameters relevant to water quality standards including:

- Understanding the basic principle of electrical conductivity measurement

- Identifying EC in water samples

- Planning and organizing testing assignment

- Using appropriate EC meters and personal protective clothing and equipment

- Understanding and applying procedures for EC testing

- Determining and reporting accurate EC results from testing.

Tools and Equipment

- EC Meter with electrode

- EC Standard 1413 µS/cm.

- Deionized water

- Glass Beaker (A Class)

### Testing of Turbidity by Turbidity Meter

Overview:This competency standard covers the skill and knowledge required to prepare samples forlaboratory testing, perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of Turbidity testing. - keeps the sample at room temperature for few minutes. - Check for the availability of Turbidity standard of10 NTU, - Identify appropriate test method, equipment and safety requirements. |
| - Prepare for laboratory testing | - Set up test equipment Turbidity meter and/or reagents in accordance with the specified work instructions. - Conduct pre-use and safety checks. - Check the calibration status of equipment. Perform calibration if required. |
| - Perform tests on samples | - Turn the meter on by pressing specific key. - Rinse the cuvette with turbidity free water and shake the sample bottle gently. - Fill the cuvette up to the mark with thoroughly agitated sample. - Wipe the cuvette thoroughly with lint free tissue, to make it free of oil drift and fingerprints. - Shake vigorously. - Place the cuvette into the cell, the mark on the cuvette cap should point towards the LCD/screen. - Run the sample as per work instructions - The turbidity value will appear on the screen. - Analyze three replicates - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean the equipment. . |
| - Quality Control Checks | - Turbidity Meter is standardized by running known standards. - Method blank is analyzed after every 10 samples - Run the Laboratory Control samples of 10 FTU/NTU with every batch of 10 samples - check repeatability by reanalyzing a pre-analyzed sample - Daily quality control data is recorded in QC Data sheet. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt precautions during work | - Rinse the cuvette with turbidity free water carefully. - Allow the sufficient time for bubbles to escape before securing the cap and do not over tighten the cap. - To obtain the sample, shake it thoroughly - Each time the cuvette is used, tighten the cap to the same degree. - Presence of debris and coarse sediments which settle down rapidlyin thecuvette will give false results. - Dirty glassware ( scratched or edge vials) could also affect readings |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Understand the basic principle of Turbidity testing

  - Identify Turbidity in water samples

  - Plan and organizing Turbidity testing equipment

  - Use appropriate Turbidity meters and accessories

  - Understand and applying procedures for Turbidity testing

  - Determine and reporting accurate and relevant Turbidity results from testing

Tools and Equipment

- Turbidity Meter

Turbidity Standard   100 NTU.

Deionized water

Glass Beaker (A Class )

Volumetric Flask 100 ml

Auto-pipette 10 ml

Lint free tissue

### Testing of Calcium & Magnesium by EDTA Titrimetric Method

Overview:This competency standard covers the skill and knowledge required to prepare samples forlaboratory testing, perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - P1: Check the sample label for the requirement of testing Calcium. - keeps the sample at room temperature for few minutes. - Check for the availability of Calcium standard solution of10 or 100 ppm otherwise prepare from 1000 ppm Stock solution through dilutions. - Identify appropriate test method, Glassware and safety requirements. |
| - Prepare for laboratory testing | - wash all glassware with washing acid and then rinse thoroughly with deionized water. - Set up the burette on burette stand properly. Fill the EDTA solution of 0.01 M in burette accordance with the specified work instructions. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Take 10 ml sample in 100 ml beaker and add 10 ml of deionized water in it as per standard. - Maintain the pH (12) of the sample with 1M NaOH and add pinch of Murexide (ammonium purpurate) indicator. - Shake it till the indicator gets dissolved and pink color is produced. - Then titrate it against the EDTA (0.01 M) as per standard. - Add EDTA solution slowly with constant stirring till the purple color appeared (end point). - Multiply the EDTA burette reading with 40, this will be equal to the calcium concentration in the sample. - Analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and store equipment. - Calculate Magnesium by using the formula - Mg=(Hardness-2.5xCa)0.243 |
| - Quality Control Checks | - EDTA concentration is verified by titrating with known standards of Ca. - Method blank is analyzed after every 10 samples - Laboratory Control samples of 10 & 100ppm Calcium analyzed with every batch of 10 samples. - check repeatability by reanalyzing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt precautions during work | - The pH of the sample should be maintained to 12. - 1M NaOH solution should be used for adjustment of pH of sample. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Understanding the basic principle of Calcium testing i.e. Identifying calcium in water samples

  - Preparations for calcium testing.

  - Using appropriate instrument and glassware

  - Understanding and applying procedures for calcium testing

  - Determining and reporting accurate calcium results from testing

Tools and Equipment

- Burette

- EDTA (0.01 M)

- NaOH (1M)

- Murexide Indicator

- Deionized water

- Glass Beaker (AClass)

- Volumetric Flask 100 ml

- Auto-pipette 10 ml

- Calcium Standard solution of 100 ppm

### Testing/Determination of Hardness by EDTA Titrimetric Method

Overview:This competency standard covers the skill and knowledge required to prepare samples forlaboratorytesting, Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Hardness. - keeps the sample at room temperature for few minutes. - Check for the availability of Hardness buffer solution - Identify appropriate test method, Glassware and safety requirements. |
| - Prepare for laboratory testing | - Wash all glassware with washing acid and then rinse thoroughly with deionized water. - Set up the burette on burette stand properly. Fill the EDTA solution of 0.01 M in burette accordance with the specified work instructions. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - Take 10 ml sample in 100 ml beaker and add 20 ml of deionized water in it as per standard. - Add 1 ml of Buffer inhibitor in sample. - Add small amount of EBT (Eriochrome black Tindicator in it and shake it till the indicator get dissolved and wine red color is produced. - Titrate the above solution against the EDTA (0.01 M) from the burette, EDTA solution should be added slowly with constant stirring till the sky blue color appeared (end point). - Multiply the EDTA burette reading with 100, this will be equal to the total hardness of the sample as per standard. - analyzed three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean the apparatus. |
| - Quality Control Checks | - EDTA concentration is verified by titrating with known standards of Ca. - Method blank is analyzed after every 10 samples - Laboratory Control samples must be analyzed with every batch of 10 samples. - check repeatability by reanalyzing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet-. - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalise work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt precautions during work | - Conduct titration at room temperature. - Always store the buffer inhibitor in amber colored bottle. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Understanding the basic principle of Calcium testing i.e.

  - Identifying Hardness in water samples

  - Preparation for hardness testing.

  - Using appropriate apparatus and glassware

  - Understanding and applying procedures for hardness testing

  - Determining and reporting accurate results from testing

Tools and Equipment

- Burette

- EDTA (0.01 M)

- Buffer Inhibitor

- Eriochrome black T Deionized water

- Glass Beaker (Class A)

- Volumetric Flask 100 ml

- Auto-pipette 10 ml

### Testing/Determination of Alkalinity by Titrimetric Method

Overview:This competency standard covers the skill and knowledge required to prepare samples forlaboratory testing., Perform tests on samples, Quality Control Checks, Record the results/ Finalize work and Adopt precautions during work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare samples for testing | - Check the sample label for the requirement of analysis of Alkalinity. - keeps the sample at room temperature for few minutes. - Check for the availability of HCl solutions - Identify appropriate test method, Glassware and safety requirements. |
| - Prepare for laboratory testing | - Wash all glassware with washing acid and then rinse thoroughly with deionized water. - Standardize the HCl 0.02 N Solution with Sodium Carbonate solution of 0.05 N - Set up the burette on burette stand properly. Fill the HCl solution of 0.02 N in burette accordance with the specified work instructions. - Conduct pre-use and safety checks. |
| - Perform tests on samples | - To 10 mL of sample few drops of mixed indicator is added and is titrated against 0.02 N HCl - Take 25 ml burette with 0.05ml resolution for titration, for low alkalinity less than 50mg/l 10ml burette with 0.02ml resolution need to be used. - Stop the titration when sample color changed to pink. - The total Alkalinity is calculated by using following formula Alkalinity, mg CaCO3/L; =; AXNX50000. 100 ml sample. Where: A = ml standard acid used N = Normality of the standard acid. - analyzed Three replicate for each sample. - Store unused reagents and dispose of wastes as required by relevant regulations and codes. - Clean and storeApparatus |
| - Quality Control Checks | - Method blank is analyzed after every 10 samples - Laboratory Control samples of 5 & 100 ppm analyzed with every batch of 10 samples. - check repeatability by reanalysing a pre-analyzed sample once a day - Daily quality control data is recorded in QC Data sheet - Results of laboratory control sample are regularly displayed in the form of control charts. |
| - Record the results/ Finalize work | - Note down the Results on analyst workbook. - Calculate uncertainty of the results - Record the results on result record form and submit to reporting section - Clear and restore work area. |
| - Adopt precautions during work | - Sodium Carbonate used for standardization should be dried before making solution at 2500C for 4 hours. - Apparatus should be thoroughly washed before analysis. - Titration must be done carefully and quickly to avoid loss of dissolved gasses during titration. - Dissolved gases can, directly or indirectly contribute to alkalinity; the gases must neither be lost nor gained during sampling, storage and titration. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

  - Understanding the basic principle of Alkalinity testing i.e.  Alkalinity is the opposite of acidity of the sample and determined by titration of the sample with a standard solution of a strong mineral acid.

  - Identifying excessive Alkalinity in water samples

  - Planning and organizing Alkalinity testing.

  - Using appropriate instrument and glassware

  - Understanding and applying procedures for Alkalinity testing in water

  - Determining and reporting accurate and relevant results from testing

Tools and Equipment

- Burette

- Hydrochloric Acid solution (0.1N)

- Hydrochloric Acid solution (0.02N)

- Sodium carbonate solution (0.05N)

- Bromocresol green + Methyl red (Mixed indicator)

- Deionized water

- Glass Beaker (A Class )

- Volumetric Flask 100 ml

- Auto-pipette 10 ml

## Water Quality Testing for Microbiological Contamination-I

### Perform Testing for Total Coliforms and Fecal Coliforms (Method-I)

Overview: This competency standards covers the skill and knowledge required toPrepare to undertake basic microbiological tests, Adopt recommended preparatory method for Coliforms, Adopt recommended preparatory method for Fecal Coliforms, Adopt recommended preparatory method for  E-coli , Perform handling or basic testing of samples for Coliforms for and fecal coliforms, perform handling or basic testing of samples  for E-coli,apply appropriate confirmation techniques,maintain environment, quality control and document control.

| Competency units | Performance Criteria |
| --- | --- |
| CU 1: Prepare to undertake basic microbiological tests | P 1: Prepare sterile environment for undertaking tests. P2: Collect samples for microbiological examination in clean, sterile, non-reactive borosilicate glass or plastic bottle. P3: Ensure that water sample is appropriate for the test requested. P4: When the sample is collected, leave ample air space in the bottle at least 2.5 cm to facilitate mixing by shaking before examination. P5: Ice samples during transport to the laboratory if they cannot be processed within 1 hour after collection. P6: Maintain samples in the dark and keep cool with ice at < 8 oC but not frozen. P7: For coliforms and E-coli analyses, the holding time from collection to analysis is 30 hour. |
| CU 2: Adopt recommended preparatory method for Coliforms | P1: Use commercially available media for detection of Coliforms following Multiple Tube Fermentation technique. P2: Prepare recommended media (Lauryl tryptose broth, LTB) double strength and single strength by weighing an amount as per supplier’s instructions using calibrated analytical balance as presumptive phase. P3: Use fifteen test tubes method for testing as per standard method. P4: Add inverted vial (durham tube) in each test tube or alternatively add 0.01 g/L bromocresol purple in media. P5: Prepare recommended media (brilliant green lactose bile broth (BGLB) for confirmed coliforms by weighing an amount as per supplier’s instructions using calibrated analytical balance as confirmed phase. P 6: Add inverted vial (durham tube) in each test tube. P7: Close tubes with metal or heat resistant plastic caps. P8: Maintain pH of media after sterilization as per manufacturer’s instruction after sterilization. P9: Autoclave media and store all sterilized media in refrigerator as per standard before use. |
| CU3: Adopt recommended preparatory method for Fecal Coliform | P1: Use commercially available media for detection of fecal coliforms following Multiple Tube Fermentation technique. P2: Prepare recommended media (EC broth) for confirmation of fecal coliforms by weighing an amount as per supplier’s instructions using calibrated analytical balance. P3: Dispense media in fermentation tubes along with inverted fermentation tubes as per standards. P4: Close tubes with metal or heat resistant plastic caps. P5: Maintain pH of media as per manufacturer’s instruction after sterilization. P 6: Autoclave media and store all sterilized media in refrigerator as per standards before use. |
| CU4: Adopt recommended preparatory method for E-coli | P1: Use commercially available media for detection of E-coli following Multiple Tube Fermentation technique. P2: Prepare recommended media (LEMB agar) for confirmation of E-coli by weighing an amount as per supplier’s instructions using calibrated analytical balance. P3: Dispense media in bottle, autoclave and maintain pH as per standards. P4: Bring medium at room temperature after autoclaving, dispense in each petri plate and allow solidifying. |
| CU5: Perform handling or basic testing of samples for Coliforms | P1: For presumptive phase,Inoculate test tubes of double and single strength of LTB media as per standards. P2: Incubate test tubes at required temperature for the growth of coliforms for 24-48 hours as per standards. P3: Colour change from purple to yellow and the gas and bubble formation in the test tubes constitute a positive test. P4: No colour change and gas formation indicate negative test. P5: For confirmation phase, shifting of positive LTB into Brilliant Green Lactose Bile Broth (BGLB) using metallic loop. P6: Incubate test tubes at required temperature for confirmed growth of coliforms into BGLB for 24-48 hours as per standards. P7: For completed phase and QC check, inoculate 10 % positive test tubes of EC medium, incubate as per standard, note the positive test tube as turbid. P8: Results are reported as MPN index/100 ml using MPN table. |
| CU6: Perform handling or basic testing of samples for fecal coliforms | P1: For fecal coliform confirmation, Shift a loopful of positive growth from LTB into EC broth, incubate for 24-48 hours at standard required temperature. P2: Report results of fecal coliforms using MPN table. |
| CU7: Perform handling or basic testing of samples for E-coli | P1: Streak LEMB agar plate using platinum loop, incubate at required temperature as per standards. P2: Growth of dark centred purple colonies, flat, with or without metallic sheen indicates E-coli colonies. |
| CU 8: Apply appropriate confirmation techniques | P1: Perform microscopic examination as per standards for the confirmation of E-coli which seems rod shape and red in colour during gram staining. P2: Perform biochemical testing as per standards i.e. IMViC test for the confirmation of E-coli. |
| CU 9: Maintain Environment and Quality Control | P1: Accept or reject media / sample based on the condition and sterility as per standards. P2: Check and maintain sterility, temperature and humidity of rooms and equipment as per standards. P3: Use controls i.e. positive and negative controls along with the tests as per standards. P4: clean and store equipment in accordance with laboratory guidelines. P5: Sterilize equipment as required P6: Store chemicals, media and controls as per standards. P7: Clean and disinfect area P8: Properly dispose contaminated waste in accordance with the standards. |
| CU 10: Document control | P1: Document test and control results in recognized format. P2: Ensure traceability of sample from receipt to reporting of results. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Understanding of the individuality of bacteria by selecting the most significant media, reagents and tests to use in studying the cultural, and biochemical activities of bacteria.

- Bacterial density is determined by the fermentation of lactose with gas and acid formation within 48 at the specific temperature.

- The technique comprises of multiple tubes and bacterial density is determined using MPN table.

- If the sample is not adequately shaken and clumps are formed then MPN value will be underestimating of actual bacterial density.

- Range and purpose of basic microbiologicalWater testing of water.

- Procedures for the use of laboratory testing equipment.

- Microbiological test procedures and  related calculations.

- Maintenance and storage of reference material of ATCC loops of E-coli and Staphylococcus aureas.

- Different microbiological testing technique for faecal indicator bacteria.

- Disposal of contaminated media and growth cultures.

Tools and Equipment

- Pre sterilized sampling bottles

- Insulated sample boxes with coolants to maintain temperature of sample at 4oC.

- Microbiological testing laboratory equipment i.e. Membrane filtration assembly, microscope.

- Equipment to maintain the required temperature for bacterial growth i.e. incubators and water baths.

- Equipment to sterilize and decontaminate the media and glassware i.e. autoclave.

- Temperature recording equipment i.e. thermometers NIST traceable.

### Perform Testing for Total Coliforms and Fecal Coliforms (Method-II)

Overview:This competency standard covers the skill and knowledge required to prepare to undertake basic microbiological tests, adopt recommended preparatory method for Coliforms and fecal Coliforms coliform performhandling or basic testing of samples for Coliforms, perform handling or basic testing of samples for fecal Coliforms,maintain environment and quality controland document control

| Competency units | Performance Criteria |
| --- | --- |
| CU 1: Prepare to undertake basic microbiological tests | P1: Prepare sterile environment for undertaking tests. P2: Collect samples for microbiological examination in clean, sterile, non-reactive borosilicate glass or plastic bottle. P3: Ensure that water sample is appropriate for the test requested as per standards. P4: When the sample is collected, leave ample air space in the bottle at least 2.5 cm to facilitate mixing by shaking before examination. P5: Ice samples during transport to the laboratory if they cannot be processed within 1 hour after collection. P6: Maintain samples in the dark and keep cool with ice at < 8 oC but not frozen. P7: For coliforms and fecal coliform analyses, the holding time from collection to analysis is 30 hour. |
| CU 2: Adopt recommended preparatory method for Coliforms | P1: Use commercially available media for detection of Coliforms following Membrane Filtration technique. P2: Prepare recommended media (m-Endo agar) by weighing the amount as per manufacturers’ instruction using calibrated analytical balance. P3: Heat to boiling the media but do not autoclave. P4: Maintain pH of media after sterilization as per manufacturer’s instruction after sterilization. P5: Bring medium at room temperature after autoclaving, dispense in each petri plate and allow solidifying. |
| CU3: Adopt recommended preparatory method for fecal Coliforms | P1: Use commercially available media for detection of fecal coliforms following Membrane Filtration technique. P2: Prepare recommended media (mFC agar) for confirmation of fecal coliforms by weighing an amount as per supplier’s instructions using calibrated analytical balance. P3: Do not autoclave the media, just heat to boiling. P4: Maintain pH of media after sterilization as per manufacturer’s instruction after sterilization. P5: Bring medium at room temperature after autoclaving, dispense in each petri plate and allow solidifying. |
| CU4: Perform handling or basic testing of samples for coliforms | P1: For coliform testing, pass recommended volume of water sample as per standards through the membrane filter using sterile membrane filtration assembly. P2: Place the membrane filter on recommended media for coliforms; incubate petri plates inverted in incubator set at the required temperature as per standard for 24-48 hours. P3: Count coliform colony as a pink to dark red color with metallic sheen .Report result in units as per standard. |
| CU5: Perform handling or basic testing of samples for fecal Coliforms | P1: Pass recommended volume of water sample through the membrane filter using sterile membrane filtration assembly for fecal coliforms as per standards. P2: Place the membrane filter on recommended media for fecalColiforms; incubate petri plates inverted in incubator set at the required temperature as per standard for 24-48 hours. P3: Count fecal coliform colony as a blue colour .Report result in units as per standard. |
| CU 6: Maintain Environment and Quality Control | P1: Adopt recommended safety precautions when handling biologically hazardous specimen. P2: Accept or reject media / sample based on the condition and sterility as per standards. P3: Check and maintain sterility, temperature and humidity of rooms and equipment as per standards. P4: Use controls i.e. positive and negative controls along with the tests as per standards. P5: Clean and store equipment in accordance with laboratory guidelines. P6: Sterilize equipment as required in standard. P7: Store chemicals, media and controls as per standards. P8: Clean and disinfect area P9: Properly dispose contaminated waste in accordance with the standards. |
| CU 9: Document control | P1: Document test and control results in recognized format. P2: Ensure traceability of sample from receipt to reporting of results. |

Knowledge and Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Understanding of the individuality of bacteria by selecting the most significant media, reagents and tests to use in studying the cultural, and biochemical activities of bacteria.

- The membrane separation process is based on the presence of semi permeable membranes.

- The principle is quite simple as the membrane acts as a very specific filter that will let water flow through, while it catches suspended solids and other substances.

- Membrane filtration method is reproducible used for large volumes and yield numeric results more rapidly than MPN.

- Useful technique for monitoring natural waters as well as drinking waters.

- Procedures for the use of laboratory testing equipment.

- Microbiological test procedures and related calculations

- Maintenance and storage of reference material of ATCC loops of E-coli and Staphylococcus aureas.

- Different microbiological testing technique for faecal indicator bacteria.

- Disposal of contaminated media and growth cultures.

Tools and Equipment

- Pre sterilized sampling bottles

- Insulated sample boxes with coolants to maintain temperature of sample at 4oC.

- Microbiological testing laboratory equipment i.e. Membrane filtration assembly, microscope.

- Equipment to maintain the required temperature for bacterial growth i.e. incubators and water bath

- Equipment to sterilize and decontaminate the media and glassware i.e. autoclave.

- Temperature recording equipment i.e. thermometers NIST traceable.

## Plumbing

### Identify plumbing Tools and Equipment

Overview:This competency standard covers the skills and knowledge required to interpret layout drawing for Plumbing Lab its specifications, its Requirement for tools and equipment.

| Competency Units | Performance Criteria |
| --- | --- |
| - Draw Layout drawing for Plumbing Lab | - Mark North Point. - Measure the Lab dimension. - Develop layout drawing - Analyze Signs, Symbols and data - Identify location for Doors and windows. - Identify instruments places. - Identify sitting plan. |
| - Identify Plumbing Tools and Equipment | - IdentifyTools and Equipment - Check for safety hazards - Conduct operational testing - Maintain professional proficiency |

Knowledge & Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Explain safety requirements, for the required tools for task.

- Explain lay out drawings with its type

- Explain different specification for tools and equipment

- Explain procedures for using different tools

- Describe different symbols for plumbing

- Describe Plumbing History and Plumbing importance

- Explain Safety measures while performing Plumbing tasks

- Explain different drawing instruments

Tools and Equipment

- Pencil

- Eraser

- Sharpner

- Calculator

- Measuring scale

- Drawing sheet

- Drawing board

- Tee Square

- Set Square

- Measuring Tape

- Computer

- AutoCAD

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Prepare layout drawing of lab

- Create sketches and drawing

- Preparation is done according to area and standards

- Prepare space for entire work

- Plan for relevant job

- Adopt safety measures

### Perform cutting, threading & reaming

Overview: This competency standard covers the skills and knowledge required to perform pipe cutting, its threading and reaming.

| Competency Units | Performance Criteria |
| --- | --- |
| - Perform Pipe Cutting. | P1. Identify tools for cutting. P2. Secure work piece firmly P3. Measure required Length P3. Use cutter OR Hacksaw P4. Loose the cutting Piece P6. Check length for cutting piece P7. Observe OHSA |
| - Perform Pipe Threading. | P1. Identify tools for threading. P2. Adopt safety measures P3. Fix work piece firmly P4. Clamp Threading die P5. Prepare threading P6. Unclamp the threading die P7. Observe OHSA |
| - Perform Pipe Reaming. | P1. Identify tools for Reaming. P2. Adopt safety measures P3. Fix work piece firmly P4. Clamp Threading pipe piece P5. Use reamer P6. Unclamp pipe piece P7. Observe OHSA |

Knowledge & Understanding.

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

- Comprehend the purpose and application of plumbing tools

- Knowledge of plumbing tools (pipe wrench, spanner, screw drivers, pipe cutters etc.)

- Knowledge of Plumbing equipment (Threading die, Hack Saw, Bench Vice, Leg Vice and reamer)

- Describe calibration of tools.

- Explain safety precaution for using tools

- Explain different type of Dies

- Explain the procedure to use of threading die

- Explain the procedure to use of Hack saw

- Explain the procedure to use of Reamer

- Explain the Clear work place

Tools and Equipment’s

- Pipe Cutting Tools,

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- PPEs

- Threading Tools

- Reaming Tools

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Define tools with it using

- Define safety measures

- Fix and Change blade for the die

- Preparation is done according to area and standards

- Prepare space for entire work

- Plan for relevant job

### Make Water Connection

Overview:This competency standard covers the skills and knowledge required to make the new connection for house from the main water.

| Competency Units | Performance Criteria |
| --- | --- |
| CU1. Prepare for water Connection | - Identify work place - Dig a pit on connection site to main water supply pipe. |
| CU2.Make water connection | - Mount the clamp over the main water supply pipe. - Set the rubber seal in the clamp - Set the ferrule at the rubber seal under the clamp - Tighten the screws of the clamp with screw wrench - Mark hole in the main pipe with centre punch and hammer - Connect the socket on the ferrule - Connect the house pipe in the socket - Fit the sluice/gate and non-return valve in the house water supply line |

Knowledge & Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

K1-Describe different tools and equipment for making new connection for water supply

K2- Explain taking connection procedure

K3- Explain cutting and threading procedures

K4.  Explain PPEs

K5.  Explain uses of different tools

K6. Explain clamps with its type

K7.  Explain use of valve while taking connection

K8.  Explain branch and main pipe

TOOLS AND EQUIPMENT

- Pipe Cutting Tools,

- Deburrers OR Reamers

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- Plungers,

- Pressure testing kits,

- PPEs

- Clamp for pipe

- Pipe (G.I OR PPRC)

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Mount pipe connection perfectly

- Use of cutting, threading and connections without leakage

- Use Safety measure at place

- Use effective tools for taking connection

- Fix clamp on main pipe

- Preparation is done according to area and standards

- Prepare space for entire work

- Plan for relevant job

### Layout for domestic water supply

Overview: This competency standard covers the skills and knowledge required for layout domestic water supply in residence and residential schemes.

| Competency Units | Performance Criteria |
| --- | --- |
| - Prepare for works | P1. Interpret work instructions P2. Plan according to job requirements P3. Organise duties P4. Select appropriate Tools and Equipment P5. Select piping materials and plumbing fixtures P6. Select PPEs |
| - Lay out for water supply scheme | P1. Mark North Point on drawing sheet P2.Measure the Scheme area. P3. Interpret layout plan by scale P4. Identify sources of water supply P5. Indicate Water Conveyance System. P6. Show storage Reservoirs P7.Locate main, sub main and branches |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Define water Layout system.

K2- Define fundamentals of water reservoirs

K3- Explain Types of water sources

K4- Describe applications of water connections with main to branches

K5- Knowledge to prepare work OR Task.

K6- Knowledge of safety measures.

K7. Explain gravity and pressure supply of water

TOOLS AND EQUIPMENT

- Pencil

- Eraser

- Sharpner

- Calculator

- Measuring scale

- Drawing sheet

- Drawing board

- Tee Square

- Set Square

- Measuring Tape

- Computer

- AutoCAD

- PPEs

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Study of different water supply system

- Installation of water supply scheme layout

- Indicate water reservoir

- Indicate gravity and pumping system

- Clarity to organise duties to perform task

### Join pipes & fittings

Overview:This competency standard covers the skills and knowledge required to prepare for different type of pipe joints and it’s fitting on residential and commercial plumbing works.

| Competency Unit | Performance Criteria |
| --- | --- |
| - Undertake pipe fitting and Installation | - Observe basic principles for pipe fittings - Identify and select materials for task - Identify tools and equipment for task - Attach Pipe with fittings - Locate fixtures properly - Undertake pipe leakage test - Use PPEs |
| - Install Hot and Cold Water Supply Pipes | - Observe basic principles for pipe fitting - Identify and select materials for task - Identify tools and equipment for task - Attach cold Pipe with fittings - Attach Hot Pipe with Geyser and fittings - Locate cross over properly - Locate drainage pipes - Undertake pipe leakage test - Use PPEs |
| - Joining Cast iron pipes | - Place the spigot end of a pipe inside the bell end of another pipe making sure that both are clean and dry. - Inert the gasket into the hub of joint using yarning iron and then pack to the proper depth by using the packing iron. - Pour the molten lead into the joint up to the top of the hub. - Perform caulking after the lead has solidified and cooled - Align the pipe - Undertake pipe leakage test - Use PPEs |
| - Join G.I Pipes | - Observe basic principles for G.I. pipes - Select materials for task - Identify tools and equipment for task - Threading & Cutting the Pipe - Tight pipe with socket - Undertake pipe leakage test - Use PPEs |
| - Join PPRC Pipes | - Observe basic principles for PPRC pipes - Adopt safety measures - Prepare welding machine with required dies of diameter. - Cut the pipes at right angles to the pipe axis using suitable cutter. - Remove any burrs or chips by cleaning the cutting area. - Heat the machine up to 260°C - Mark the welding depth on pipe - Insert the end of pipe into the heating sleeve up to the marked welding depth and mount the fitting also. - Leave the pipe and fitting on the heating tool until the heating time is elapsed (5 to 7 sec) - Remove the pipe and fitting from heating tool and push them immediately into each other up to marked welding depth without rotating. - Allow the joint to cool down. |
| - Joining PVC Pipes | - Clean the ends of pipes to be joined. - Make one end of pipe should be cup/bell/ socket type if they are not in required shape. - Apply jointing solution in the bell/socket and over the spigot end - Insert the spigot end of a pipe into bell/socket of other pipe |
| - Joining Concrete Pipes | - Correctly position and bed the first pipe. - Prepare the bedding for the second pipe. - Apply the seal on the spigot end. - Ensure the joint ring is not twisted and correctly located on spigot. - Centre the socket/bell and fill the gap with cement mortar |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Knowledge of Safety requirements for installing cold and hot water pipes in residential buildings.

K2.  Knowledge of Fittings attach with hot water

K3.  Explain signs and symbols for Water supply system

K4.   Explain specifications for cold and hot water connections

K5-   Knowledge of faults in hot water pipes

K6-   Explain safety values use in geysers

K7.   Explain the equipment for installing and fittings of pipes

K8.   Explain drain Pipes

K9.  Explain method for different type of pipe joints

TOOLS AND EQUIPMENT

- Pipe Benders,

- Pipe Cutting Tools,

- Deburrers,

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- Pressure testing kits,

- PPEs

- Hot water fittings

- Hot water accessories

- G.I. & Cost Iron Pipes according to specifications

- Pipe Vice

- Hack Saw with blade

- Different Fittings

- Geyser

- Safety Valve

- Cost Iron Pipe

- Lead

- PPRC Pipe with fittings

- Cocking Tools

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Explain safety requirements at work place

- Prepare plan for installation/replacement

- Performing installation/replacement

- Perform fittings for installation of geyser

- Perform different pipe fittings methods.

- Perform working of drains

- Perform safety measures

- Perform different pipe joints

### Install plumbing fixtures

Overview:This competency standard covers the skills and knowledge required to install plumbing fixtures at work place i-e installation of water closet, flushing cistern, Wash hand Basin, English WC and Urinal

| Competency Units | Performance Criteria |
| --- | --- |
| - Install Wash Hand Basin | - Identify safety requirements for installation - Identify tools for work - Identify Fixtures - Perform measurements - Mark out Installation point - Turn the water supply off of the concerned section. - Mark and drill pilot holes for the floor fixing screws. - Mark, drill and plug the wall holes for basin fixing screw - Install tee stop cock at the end of water supply pipe (hot and cold) - Connect the flexible rubber connection pipes with pillar cocks or mixture - Fit the couplene in the hole of basin. Fit floor trap under the waste pipe and adjust waste pipe with it. - Re-position the pedestal and screw it into proper place. - Position the basin and check its level then screw the basin to wall. - Inject silicon sealant for sealing. - Tighten the pedestal screws. - Turn on the water supply and check for leaks. |
| - Install English water closet | - Mark out Installation point - Compact and Level the floor at the place of installation of water closet. - Place P-trap at compacted and levelled surface. - Place the W.C pot on the trap in leveled surface and provide support to it. - Fill the P-trap with cement and cloth bandage soaked in cement solution. - Connect soil pipe to P-trap - Connect tee with soil pipe outside the toilet wall. - Joint the vent pipe with small end of tee. - Connect larger end of soil pipe to septic tank. - Attach flush pipe in to the pot hole. - Drill holes at the required place and height for flushing cistern. - Install flushing with screws and joint it with flush pipe. - Fill the earth to required level. - Finish conglomerate floor or tile flooring |
| - Install Flushing Cistern | - Mark out Installation point - Measure height for flushing cistern - Drill holes at the required place and height for flushing cistern. - Install flushing with screws and joint it with flush pipe - Fix flushing pipe - Connect inlet pipe with water supply - Perform final quality inspection - Check Level - Use PPEs |
| - Install Urinal | - Mark out Installation point - Turn the water supply off of the concerned section. - Install adequate support for wall hangers and install wall hangers if needed. - Drill the holes at two feet height and drill the holes. - Determine the position for waste pipe nipple - Apply thread sealant tape. - Install female collar to the waste pipe. - Place the gasket on the female collar with the beveled surface facing away from the collar. - Position the urinal on the wall hangers and screwed them. - Secure the urinal bottle trap and waste pipe to female collar using the screws. - Install the flush valve according to manufacturer instructions. - Connect the water supply and complete waste pipe connection. - Turn on water supply. - Flush and check the entire installation for leakage |
| - Install Sink | - Mark out Installation point - Measure height for sink - Install adequate support for wall hangers and install wall hangers if needed. - Fix sink fat measured height with drain pipe - Connect inlet pipe with water supply - Perform final quality inspection - Check Level - Conduct Operational Testing - Use PPEs |
| - Install Bath Tub | - Mark out Installation point - Measure Height for bath tub - Set and level Bath Tub at designated place - Install a ledger board for supporting tub - Secure the tub to studs according to manufacturer instructions. - Attach drain to tub - Connect the overflow drain - Connect the drain pipe with P-trap - Connect inlet pipe with water supply - Perform leakage test - Perform Safety Precaution - Use PPEs |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Knowledge of water closet, Flushing Cistern with its types

K2- Use of tools and equipment’s

K3- Knowledge of joining techniques and with fixtures

K4- knowledge of levelling and fixing WC

K5. Knowledge of WC with its types

K6. Knowledge traps fittings

K7. Explain wash hand basin Pedestal type

K8. Explain fitting procedure to install wash hand basin

TOOLS AND EQUIPMENT

- Pipe Benders,

- Pipe Cutting Tools,

- Pipe vice with stand,

- Deburrers,

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- Plungers,

- Pressure testing kits,

- PPEs

- P-Trap

- W.C (Indian & English)

- Wash hand basin

- Shower

- Geyser

- Bolt Kit

- Screws

- Clamps

- Nails

- Hammer

- Bath Tub with accessories

- Mallet

- Urinal with fitting

- Urinal Cistern

- Tee cock

- Pillar cock

- Sink with mixer

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Fix and use of water closet and flushing cistern

- Demonstrate the installation of water closet and flushing cistern

- Install wash hand basin and Shower

- Install geyser with its fitting and valve

- Fix trap and measure the size

- Install Urine with water supply pipe

### Install & repair water pumps

Overview: This competency standard covers the skills and knowledge required to install drinking water pumps and its repair work.

| Competency Units | Performance Criteria |
| --- | --- |
| - Install Air ejector Pump | P1. Mark out Installation point P2.Perform Safety Precaution P3. Measure Pipes with fittings P4. Fix pump with suction & delivery pump P5. Connect with electricity P6. Perform leakage test P7. Use PPEs |
| - Install Centrifugal Pump | P1. Mark out Installation point P2.Perform Safety Precaution P3. Measure Pipes with fittings P4. Fix flanges with suction & delivery pipes P5. Connect with electricity P6. Perform leakage test P7. Use PPEs |
| - Install Rotary Pump | P1. Mark out Installation point P2.Perform Safety Precaution P3. Measure Pipes with fittings P4. Fix flanges with suction & delivery pipes P5. Connect with electricity P6. Perform leakage test P7. Use PPEs |
| - Carry out repair of Pump | P1.Perform Safety Precaution P2. Disconnect electricity and pump P3. Use PPEs P4. Check for Fault P5. Repair it P6. Refit with suction & delivery pipes P7. Connect with electricity P8. Perform leakage test |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

- Use of tools and equipment’s.

- Knowledge of joining techniques and pipe fittings

- Knowledge of leakage in pipes and pumps

- Explain working of different pumps

- Explain repair for different pumps.

- Explain safety measures while performing repair of works

- Explain leakage checking with its methods

TOOLS AND EQUIPMENT

- Pipe Benders,

- Pipe Cutting Tools,

- Chain Pipe Wrench

- Deburrers,

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- Plungers,

- Pressure testing kits,

- Radiator tools

- PPEs

- Different Pumps with fittings

- Electricity

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Fit and refit the pump

- Install different pumps with its fittings

- Install flanges with pumps and pipes

- Check for leakage

### Install turbine pumps

Overview: This competency standard covers the skills and knowledge required to Install turbine

| Competency Units | Performance Criteria |
| --- | --- |
| CU1.Install turbine | P1. Mark out Installation point P2. Use PPEs P3. Check depth of bore P4. Adopt Safety Measures P5. Measure turbine Pipes with fittings P6. Fix Turbine with flange &Pipes P7. Insert turbine into bore with tripod & chain pulley P8. Connect Motor with shaft fittings P9. Connect electricity and start P10. Remove tripod P11. Check discharge |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out tasks covered in this competency standard. This includes the knowledge of:

K1- Knowledge of turbine with its working

K2- Explain Use of tools and equipment’s for its fitting

K3- Explain different joining techniques and pipe fittings

K4- Knowledge of leakage testing

K5. Explain turbine impellers with its fittings

K6.  Explain installation method into bore.

K7.  Explain tripod and chain pulley function

TOOLS AND EQUIPMENT

- Pipe Cutting Tools,

- Chain Pipe Wrench

- Deburrers,

- Plumbing pliers,

- Plumbing wrenches,

- Plumbing spanners,

- Plungers,

- Pressure testing kits,

- Radiator tools

- PPEs

- Turbine with impellers & Motor

- Electricity

- Turbine pipe with fittings

- Pipe wooden / steel clamps

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- use of turbine

- Installation of Turbine

- Discharge finding

- Install tripod with chain pulley

- Function of Chain pulley

### Prepare sketches of aqueducts & water pipes

Overview:This competency standard covers the skills and knowledge required to prepare an aqueduct / watercourse constructed to carry water from a source to a distribution point far away. In modern engineering, the term aqueduct is used for any system of pipes, ditches, canals, tunnels, and other structures used for this purpose.

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Prepare Sketch for aqueduct | P1. Identify aqueduct. P2. Spread & fix sheet P3. Apply scale P4. Draw aqueduct |
| CU-2. Assemble G.I pipes | P1.Clean pipes surface P2.Carry out Lubrication on edges P3. Apply Threading P4.Equalize gasket P5.Perform alignment P6. Join pipes P7.Perform final quality inspection (Testing) |
| CU-3. Assemble concrete pipes | P1.Clean pipes surface P2.Carry out watering on edges P3. Apply sealant P4.Equalize gasket P5.Perform alignment P6. Join pipes P7.Perform final quality inspection |
| CU-3. Assemble PPRC pipes | P1.Clean pipes surface P2.Carry out Heating on edges P3. Apply sealant P4.Perform alignment P5. Join pipes P6.Perform Test for joints |

Knowledge & Understanding.

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard:

K1. Comprehend the purpose and application of aqueduct

K2 Knowledge of aqueduct parts

K3. Explain design procedure for aqueduct

K4- Describe working of Aqueduct.

K5.  Explain different type of pipes use in water supply system

K6. Describe different pipe jointing methods.

K7. Describe safety procedure for joining pipes

K8. Explain PPRC pipes with it joining methods

K9. Explain concrete & Cast iron difference

TOOLS AND EQUIPMENT’S

- Pipes

- Calculator

- Thermometer

- Valves

- Pipe repairs,

- Plungers,

- Pressure testing kits,

- Radiator tools

- Spirit level

- PPEs

- Drawing sheet with drawing instruments

- Sealant

- Gasket

- Threading die

- Pipe Vice

- Flanges

- Pipe cutter

- Wrench set

- Scale card

- Spanner set

- Clamps

- Nuts & Bolts

- Spring Washers

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Define Joints, Pipes and Aqueduct.

- Draw sketch of aqueduct for different sizes.

- Design an aqueduct

- Design pipe joint aspects

- Plan safety procedure during design and drawing

- Plan the steps to join cast iron pipes

- Plan the stages to join PPRC pipes

### Plan Water Distribution System

Overview: This competency standard covers the skills and knowledge required to interpret water distribution system, interpret layout for water distribution network, Interpret layout for water Storage Reservoir, Interpret storage capacity of Reservoir and Accumulate Hydraulic model

| Competency Units | Performance Criteria |
| --- | --- |
| CU-1. Interpret water distribution system | P1. Identify safety requirements for installation P2. Identify Gravity system P3. Identify Pumping system P4. Identify partly gravity & pumping system |
| CU-2. Interpret layout for water distribution network | P1. Mark out distribution network points P2.Identify dead end system P3. Identify Radial system P4.Identify Ring System P5. Identify Grid Iron System |
| CU-3. Interpret layout for water Storage Reservoir | P1. Mark out place for reservoir P2.Identify surface reservoir P3. Identify elevated reservoir P4. Monitor difference in working both reservoir P5. Perform cleaning / repair process for reservoir |
| CU-4. Interpret storage capacity of Reservoir | P1. Identify quantity of water for reservoir P2.Identify balancing storage P3. Identify breakdown storage P4. Calculate Fire demand storage P5. Identify dead storage |
| CU-5. Accumulate Hydraulic model | P1. Evaluate methodology of distribution system P2.Develop pipe networks into sub networks P3. Recognize Data P4. Prepare hydraulic model P5.Analyze Results |

Knowledge & Understanding

The candidate must be able to demonstrate following underpinning knowledge and understanding required to carry out tasks covered in this competency standard.

K1- Knowledge of water storage reservoir

K2- Explain Uses of tools and equipment to clean and repair of water reservoir

K3. Explain different system for water supply in housing scheme

K4. Explain different system for water supply Pipe laying network in housing scheme

K5- Knowledge of joining techniques and pipe fittings to reservoir

K6- knowledge of levelling and leakage repairing in water supply system

K7. Explain type of reservoir according to shapes, material and design

K8. Explain reservoir storage parts frequently

K9. Explain hydraulic model

TOOLS AND EQUIPMENT

- Drawing sheet

- Drawing instruments

- Pencils

- Eraser

- Compass

- Sprit level

- Calculator

- Umbrella (Optional)

- PPEs

Critical Evidence(s)

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Plan a storage reservoir

- Plan site selection for reservoir

- Demonstrate the installation of reservoir pipes

- Demonstrate pipe laying & distribution system

- Plan storage capacity for water reservoir

- Plan distribution