National Competency Standards Level 2

Electrical  Technology (Domestic/General Electrician)

Equivalent to G-III

60 Credit Hours

National Vocational and Technical Training Commission (NAVTTC)

Government of Pakistan

Table of Contents

Introduction	3

Purpose of the Qualification	4

Summary of Competency Standards and contact hours	4

Packaging of Occupations	5

Date of Validation	5

Date of Review	5

Codes of Qualifications	5

Members of Qualifications Review Committee	6

Members of Qualifications Development Committee	6

Members of Qualification Validation Committee	7

Entry Requirements	7

Detail of Competency Standards	8

0713E&E1	Follow Occupational Health and Safety Practices	8

0713E&E2	Demonstrate Basic Communication Skills	11

0713E&E3	Prepare Estimates for Electrical Work	13

0713E&E4	Follow basic green practices for Domestic/General Electrician	15

0713E&E5	Install single-phase Electrical wiring.	16

0713E&E6	Perform Testing of Electrical Wiring	20

0713E&E7	Install Security & Electrical Communication Systems	24

# Introduction

Green skills incorporation in TVET aims to build capacity of skilled workforce, which is aware of environmental hazards and accordingly adopts more sustainable and environment friendly practices at the workplace. The workforce that possesses competencies and relevant knowledge & understanding oriented to green occupations is more employable and become an asset for businesses, enterprises and communities in developing green economies that results in improved human well-being and reducing environmental risks.

The United Nation’s Sustainable Development Goals (SDGs), UNESCO ESD initiatives UNEVOC, ILO, CPSC and ADB guidelines, studies and training manuals provide comprehensive green skill strategies to develop competencies / skills that can be imparted under vocational education and training. They are focused to prepare the workforce to adopt sustainable practices and address environmental degradation by appropriately managing human and material resources.

The vocational professions are increasingly getting attention in Pakistan, not only among the youth seeking to enter in the job market but also among adults who wish to polish their skills to develop a career out of it. The scope and demand of Domestic or General Electrician is very high in Pakistan due to fast growing population and construction projects in Pakistan. There are more job opportunities for electricians in Pakistan than any other vocational field. Pakistan is still facing energy crises, therefore needs more power houses, dams, renewable energy sources, solar installations etc. which will result in more demand of electrical technicians. Pakistan can boost economic growth and job creation by overcoming inefficiencies in its power sector. Power sector reforms that address these distortions can make better use of existing facilities. These need to focus on eliminating waste, promoting the shift towards cleaner energy and attracting private investments.

The Government of Pakistan through National Vocational & Technical Training Commission (NAVTTC) in collaboration with German Development Company & BMZ has revised the national vocational qualifications for NVQF level 1 to Level 3 in Electrical Technology with greening concepts, which not only allows trainees to equip with growing Industrial trends but will be beneficial in Rapidly capturing the job market across the globe.

This document identifies competencies related to electrician trade identified by the relevant industry during workshops held at Lahore Chamber of Commerce & Industry, Lahore. These skills either can be infused as a separate competency standard / competency unit in relevant qualifications or can be integrated as a separate module in the qualifications already developed or being developed under growth economic sectors. Critical evidence statements have also been added to assist assessors in preparation and conduct of assessment. The purpose of this document is to bring change in abilities, values and attitudes needed by human to support the sustainable and effective utilization of resources in the workplace. It focuses on the skills that will help preserve and conserve the environment. If qualifications implemented by training providers, will directly benefit the poor by increasing access, improving reliability, and reducing cost and pollution.

This qualification can create a considerable impact in electrical field especially in the following areas:

- Energy saving infrastructures

- Renewable Energy

- Building Automation

- Energy Network Management

- e-Vehicles

- LED Illumination

- Solar Energy

Structural changes will realign sectors that are likely to decline as a result of the greening of the economy and workers will need to be retrained accordingly. The successful transition to a low-carbon economy will only be possible if workers can flexibly adapt and practice to go green as per their industry standards.

# Purpose of the Qualification

The qualifications are in line with the vision of Pakistan’s National Skills Strategy (NSS), National TVET Policy and National Vocational Qualification Framework (NVQF) based on demand of respective employers. This provides policy directions, support and an enabling environment to the public and private sectors to impart training for skills development to enhance social and economic profile. The National Competency Standards could be used as a referral document for the development of curricula and Assessment Packages to be used by training institutions and Qualification Awarding Bodies respectively.

The purpose of the training is to provide the Green skills to the trainees in the field of Electrical and convert it into value added product, which is acceptable by International market and fit-in a skilled graduate into National Vocational Qualification Framework for his / her vertical career progression and qualification equivalencies at par with acceptable international standards.

# Summary of Competency Standards and contact hours

| Competency Standards | Category | Estimated Contact Hours |  |  | Cr Hr |
| --- | --- | --- | --- | --- | --- |
|  |  | Th | Pr | Total |  |
| Follow Occupational Health and Safety practices | Functional | 8 | 32 | 40 | 4 |
| Demonstrate basic communication skills | Generic | 12 | 38 | 50 | 5 |
| Prepare estimates for electrical work | Functional | 16 | 64 | 80 | 8 |
| Follow basic green practices for Domestic/General Electrician | Generic | 8 | 32 | 40 | 4 |
| Install Single Phase Electrical Wiring | Technical | 60 | 250 | 310 | 31 |
| Perform Testing of Electrical Wiring | Technical | 8 | 32 | 40 | 4 |
| Install Security and Electrical Communication systems | Technical | 8 | 32 | 40 | 4 |
| Total |  | 120 | 480 | 600 |  |

# Packaging of Occupations

The National Vocational Qualification for General Electrician / Domestic Electrician has been packaged as detailed below:

- Follow Occupational Health and Safety practices.

- Demonstrate Basic Communication Skills.

- Prepare estimates for Electrical Work.

- Follow basic green practices for Domestic/General Electrician.

- Install Single Phase Electrical Wiring.

- Perform Testing of Electrical Wiring.

- Install Security and Electrical Communication System.

# Date of Validation

The National Competency Standards Level-2 for Electrical Technology “Domestic/General Electrician”

has been validated by the Qualifications Validation Committee (QVC) members on 12 April, 2023 and will remain valid for ten years i.e. 11 April, 2033.

# Date of Review

The National Competency Standards Level-2 for Electrical Technology “Domestic/General Electrician”

has been validated by the Qualifications Validation Committee (QVC) members on 12 April, 2023 and shall be reviewed after three years i.e. 11 April, 2026.

# Codes of Qualifications

The International Standard Classification of Education (ISCED) is a framework for assembling, compiling and analyzing cross-nationally comparable statistics on education and training. ISCED codes for these qualifications are assigned as follows:

| 0713E&E(2) | National Vocational Certificate Level 2 in Electrical Technology |
| --- | --- |

# Members of Qualifications Review Committee

The following members participated in the qualification review committee of this qualification held at Lahore Chamber of Commerce & Industry Lahore:

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Mr. Shehreyar Khan Marwat | AD Acad/Oper | KP- TEVTA, Peshawar |
| 2 | Mr. Rehan Qureshi | Instructor GTTI | P-TEVTA, Lahore |
| 3 | Mr. Waqas Niaz | SDO | NTDC, Islamabad |
| 4 | Mr. Yusuf Mirza | Deputy Director | CoE / GSTC Mughalpura, Lahore |
| 5 | Mr. Taha Rehman | Sr. Engineer | Delta Electromechanical Works, Islamabad. |
| 7 | Engr. Muhammad Aleem | DACUM Facilitator | Professor UoL, Sargodha |
| 8 | Mr. Muhammad Aasim | NAVTTC Coordinator | NAVTTC HQs, Islamabad |
| 9 | Mr. Hassan Abbas | XEN | IESCO, Islamabad |
| 10 | Syed Waqar Azeem | Director Curriculum | P-TEVTA, Lahore |
| 11 | Hafiz Waqar Hashmi | AD Curriculum | P-TEVTA, Lahore |
| 12 | Mr. Basit Ali | AD Curriculum | PVTC, Lahore |
| 13 | Mr. Atif Mahmood | Technical Advisor | GIZ, Islamabad |
| 14 | Mr. Muhammad Naeem Akhtar | Technical Advisor | GIZ, Islamabad |

# Members of Qualifications Development Committee

The following members participated in the qualification development of this qualification:

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Mr. Aijaz Ahmed Zia | Design & Application Engineer | INTECH Process Automation. Lahore |
| 2 | Mr. Amir Amin | HOD Electrical, Research Associate LUMS | City Polytechnic, Lahore |
| 3 | Mr. Muhammad Faheem Anjum | Chief Instructor Electrical | P-TEVTA, Lahore |
| 4 | Mr. Muhammad Asad | Instructor Electrical | P-TEVTA, Lahore |
| 5 | Ms. Tahreem Javeed | Lab Engineer | The University of Lahore |
| 6 | Ms. Huma Naeem | Research Associate | COMSATS Lahore |
| 7 | Engr. Inayat Ur Rehman | DACUM Facilitator | KPK-TEVTA, Peshawar |
| 8 | Mr. Muhammad Yasir | NAVTTC Coordinator | NAVTTC HQ Islamabad |

# Members of Qualification Validation Committee

The following members participated in the qualifications validation of this qualification:

| S# | Name | Designation | Organization |
| --- | --- | --- | --- |
| 1 | Mr. Israr Ahmad | DD Academic | KP-TEVTA, Peshawar |
| 2 | Mr. Muhammad Yasir | NAVTTC Coordinator | NAVTTC HQ Islamabad |
| 3 | Ms. Sayeda Fatima Iqbal | System Analyst | PBTE Lahore |
| 4 | Mr. Danish Khan | Calibration Engineer | NPSL(PCSIR) Islamabad |
| 5 | Mr. Ghulam Rasool Maka | Vice Principal | S TEVTA, Karachi |
| 6 | Mr. Muhammad Mehboob Butt | Associate Professor | P TEVTA, Lahore |
| 7 | Mr. Inayat Ur Rehman | EX Professor / Director Academics | KP-TEVTA, Peshawar |
| 8 | Mr. Muhammad Asad | Instructor Electrical | P-TEVTA, Lahore |

# Entry Requirements

The entry level for National Vocational Certificate Level 2 in Electrical Technology is Middle Grade 8 certificate.

# Detail of Competency Standards

### Follow Occupational Health and Safety Practices

Overview:

After this Competency Standard, the Trainee will be able to develop skill and competence required to maintain Occupational Health and Safety and take remedial measures to deal with the emergencies in a professional manner, thus minimizing the losses and providing a safe and healthy working environment. The learner will also be able to practice green skills and become more environmental friendly.

| Competency Units | Performance Criteria |
| --- | --- |
| - Ensure use of personal protective equipment (PPE) | - Arrange the required personal protective equipment - Check functional condition of PPE’s - Wear personal protective equipment - Store PPE at appropriate place after use. |
| - Maintain First-aid Box | - Ensure availability of first aid box - Check requisite first aid box for r emergency - Check expiry of medicines - Perform first aid treatment against electric shocks - Perform first aid treatment/bandages against minor injuries. - Develop a waste management plan for first aid supplies, including proper disposal hazardous materials. - Promote the use of recyclable materials in the procurement of first-aid box. |
| - Oparate Fire Extinguisher | - Asses the fire situation. - Select the fire extinguisher based on the type and size of the fire. - Verify the working condition of the fire extengusher, ensuring it is properly pressurized and has a vilid inspection tag or seal. - Apply appropriate fire extinguishing technique such as using the PASS method (Pull, Aim, Squeeze, Sweep) for extngueshing the small fire - Check expiry of fire extinguisher - Operate fire extinguisher |
| - Ensure Safeguard of Machines | - Maintain radiator shield - Maintain alternator fan shield - Maintain heat resister material on silencer - Cover main circuit breaker - Lock canopy doors |
| - Adopt company policies and procedures | - Ensure company’s safety policy - Adopt company safety procedure - Advocate worker with company safety policy - Implement Safety sign board as per standard |
| - Attain health & safety training | - Take required health and safety training - Implement work hazardous material information system (WHMIS) - Adopt first aid cardio respiratory, resuscitation and CPR |
| - Prepare for emergencies | - Take emergency response training - Ensure practice of emergency exercises - Check the emergency alarms - Ensure regular practice of gathering the workers in assembly area during the emergency. |
| - Respond to emergencies | - Follow emergency plan - Communicate instructions to co workers - Assess risk and determine course of action - Operate emergency equipment and supplies - Ensure that the ambulance is at stand by(for emergency) |

Knowledge & Understanding

- Factors affecting Health & Safety in the workplace.

- Personal Protective Equipment (PPE)

- First-Aid-Box.

- Emergency medicines and expiry

- Methods of treatment against electric shock

- Methods of treatment against minor injuries

- Types of Fire Extinguisher

- Uses of Fire Extinguisher

- Safety measures

- Types of work site Hazards

Tools and Equipment

| SN | Tools |
| --- | --- |
| 1 | Protection suite |
| 2 | Safety shoes |
| 3 | Safety goggles |
| 4 | Hearing protection |
| 5 | Respiratory mask |
| 6 | First Aid Box |
| 7 | First Aid Kit |
| 8 | Stretcher |
| 9 | Fire Buckets |
| 10 | Fire Extinguisher |
| 11 | Emergency Alarm/Bell |
| 12 | Emergency response Plan |
| 13 | Fall Protection Plan |

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Types of hazards that are most likely to cause harm to health and safety

- Health and safety signs and precautions

- Techniques and methods to identify the risks of hazards at workplace

- Safety reporting procedures and documentation

- Describe fire-fighting methods

- Demonstrate use of appropriate Personal Protective Equipment (PPE) for the assigned job

- Demonstrate removal and disposal of PPE.

### Demonstrate Basic Communication Skills

Overview:

This Competency Standard identifies the competencies required to apply communication skills at workplace in accordance with the organization’s guidelines and procedures. You are expected to work in a team to achieve common organizational goals and avoid conflicts. This competency standard would also enable you to use basic computer skills to communicate effectively and prepare work related documents and reports. This module also focuses on establishing a green environment by adopting paperless communication medium and emphasis more on digital skills.

| Competency Units |  | Performance Criteria |  |  |
| --- | --- | --- | --- | --- |
|  | CU1. Work in Team | P1. Treat team members with respect and maintain |  |  |
|  |  |  |  | Positive relationships to achieve common |
|  |  |  |  | organizational goals. |
|  |  | P2. P3. |  | Note the instruction. Comply with the Instructions |
|  |  | P4. |  | identify interrelated work activities to avoid |
|  |  |  |  | confusion |
|  |  | P5. |  | Adopt communication skills appropriate to work |
|  |  |  |  | activities and company procedures |
|  |  | P6. |  | Identify problems and resolve them through |
|  |  |  |  | discussion and mutual agreement. |
|  | CU2.Deal with Clients | P1. | Collect Demand from clients. |  |
|  |  |  | using appropriate communication procedures |  |
|  |  | P2. | Negotiate with client regarding wages, time, labor requirements. |  |
|  |  | P3. | Develop consensus with the Clint. |  |
|  | CU3. Demonstrate Basic IT | P1. Create files and folder in Microsoft Word P2. Demonstrate major commands of operating system/windows P3. Create document P3. Edit document P4. Create tables in Microsoft Word P5. Insert header and footer, footnotes, and page number etc. P6. Create table of contents P7. Print document P8. Use appropriate e-media internet for sending/receiving emails |  |  |

Knowledge & Understanding

The candidate must be able to demonstrate fundamental knowledge and understanding required to carry out the tasks covered in this competency standard. This includes the knowledge of:

- Principles of effective and interactive communication 7 C’s of communication and their importance.

- Cultural and organizational practices for effective communication Effective negotiation skills.

- Role of team members and functionality of the teams Team dynamics and stages of team development Conflict resolution strategies.

- Negotiation Skills.

- Basic architecture of computer system.

- Input / output devices of computer and their functions.

- Basic computer skills using MS Word, MS Excel, use of internet, sending and receiving emails etc.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Communicate effectively with colleagues and clients.

- Develop a job completion report for the work using computer technology

### Prepare Estimates for Electrical Work

Overview:

| Competency Units | Performance Criteria |
| --- | --- |

This competency standard identifies the competencies required to prepare estimates in accordance with client’s guidelines. The Trainee will be expected to estimate, ensuring cost effectiveness, conforming to standards and regulations. The underpinning knowledge regarding calculations and estimation will be sufficient to provide the basis for your work. Module is also focused to re-think more about green practices while calculating and developing basic drawings.

| CU1.Develop Basic Drawing | - Collect information - Take accurate measurements regarding work specifications - Develop drawing according to job requirement - Use relevant electrical symbols and signs as per standards - Confirm the job specifications and drawing from client or supervisor - Make necessary adjustments, where required - Calculate electrical load based on the electrical installations provided in the specifications |
| --- | --- |
| CU2. Perform Estimation of material | - Identify requirements of the material(s) to be utilized for the work in accordance with the job specifications and drawing - Check and confirm the requirement of the materials from the client or supervisor for accurate estimation. - Quantify the material as per drawing - Use appropriate methods to calculate the of cost of material and accessories keeping in view the current market prices - Check and present the cost estimate to the client or supervisor for agreement |
| CU3. Calculate Labor Cost | - Make necessary adjustments in estimates, where required. - Calculate hours required for the task in accordance with the job requirements - Prepare labor cost for the task using appropriate procedures. |

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out the tasks covered in this competency standard. This includes the knowledge of:

- Basic electrical terminologies Electrical Circuit Characteristics Basic electric formulas & numeracy.

- Norms in interacting & negotiating with customers/clients Interpretation of layout plans/wiring diagrams, service manuals and manufacturer’s specifications, technical sketches, graphic symbols etc.

- Types of electrical control and protective switchgear and accessories used in electrical circuits

- Types of electrical wires and cables and their ratings.

- Types of electrical conduits, casing and capping etc. their applications and their cutting/jointing/fixing methods.

- Types of insulation material used in electrical installations Types of earth electrodes and their applications.

- Norms and standard formats of preparing estimates

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Provide cost effective and quality oriented Bill of Quantities (BOQs).

- Make the rate analysis according to market prices.

- Provide the estimate in accordance with the BOQs.

### Follow basic green practices for Domestic/General Electrician

Overview

This competency standard will provide skill, knowledge and attitude required to ensure the basic green practices in the Electrical Field.

| Competency Units | Performance Criteria |
| --- | --- |
| - Help in organizing working environment | Trainee must be able to: - Clean all equipment/machinery - Clean whole workplaces/work sites as instructed by management. - Maintain tools and equipment Regularly - Store equipment/machinery Properly as instructed by management. |
| - Perform disposal of electrical waste in designated area as per SOP | Trainee must be able to: - Segregate disposable and non-disposable material - Segregate materials according to disposal SOP - Dispose waste accordingly at allocated site. - Clean the workplace. |
| - Reuse training material (consumables) | Trainee must be able to: - Collect used material after performing tasks. - Segregate the useful material from the waste. - Store the useful material at appropriate storing place for reusing. |
| - Comprehend knowledge of Renewable Energy Recourses | Trainee must be able to: P1. Demonstrate Solar, Wind, Hydro, Geothermal energy etc. for alternate energy source. P2. Promote the use of natural sunlight more instead of artificial lights. P3. Use low carbon emission vehicles and machines |
| - Practice Green Skills at Workplace | Trainee must be able to: P1. Turn off extra lights and putting signs to switch off lights before leaving the room etc. P2. Minimize the use of plastic bags and other hazardous materials. P3. Use LED lights instead of other bulbs for power saving. P4. Minimize the use of paper P5. Use e-channel for communication |

Knowledge & Understanding

- Steps involved in cleaning of work sites.

- Different types of waste disposal bins.

- Steps involved in recycling the waste.

- Basic information of renewable energy resources.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Demonstrate disposal of different types of electrical waste accordingly

- Demonstrate use of energy saving signs at work sites

### Install single-phase Electrical wiring.

This competency standard identifies the competencies required to install single phase domestic wiring according to the client’s demand. The trainee will be able to Maintain Tools & Equipment for Single Phase Wiring, Make Cable/Wire Joints for Single Phase Wiring, Prepare and Install Distribution Boards for Single Phase, lay cables, practice single phase electrical circuits and Perform single phase electrical domestic wiring. Module is also focused to re think more about green practices while installing single phase electrical wiring.

| Competency Units | Performance Criteria |
| --- | --- |
| - Maintain Tools & Equipment for Single Phase Wiring | - Identify tools and equipment - Prepare list of tools and equipment as per requirement - Arrange Tools and Equipment - Interpret job card - Insulate Tools and Equipment - Calibrate measuring tools - Manage Inventory of tools and equipment - Maintain Tool Box |

| Competency Units | Performance Criteria |
| --- | --- |
| - Make Cable/Wire Joints for Single Phase Wiring | - Select the cable. - Strip the wire according to 50mm. - Make Cross/Twist joint - Make Straight/Married joint - Make T- Joint - Make Rat tail joint - Make Britannia joint |
| Competency Units | Performance Criteria |
| - Prepare and Install Distribution Boards for Single Phase | - Develop Basic Drawing - Prepare estimate for wiring material. - Prepare Distribution Board - Install Distribution Board. - Test Distribution board. |
| Competency Units | Performance Criteria |
| CU4. Lay cables | P1 Interpret electrical drawing/document P2. Identify cables P3. Lay cables P4. Perform earthling |
| CU5. Practice single phase electrical circuit | - Draw wiring diagram of single phase circuit. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply |
| CU6. Perform single phase electrical domestic wiring. | - Draw wiring diagram for single phase. - Draw Current path diagram for single phase. - Draw layout diagram for single phase. - Mark on working board according to layout diagram. - Install accessories according to layout diagram. - Lay wires in duct/pipe according to layout diagram. - Make connections according to wiring diagram. - Check the circuit before connect the main supply. - Make connection with main supply. - Check the function of circuit after connect the main supply |

Knowledge & Understanding

- Explain Various tools and equipment and their functions

- Define Job card/work order

- How an Arrangement of tools/equipment as per job is required?

- Differentiate between corrective and preventive maintenance

- Arrange tools and equipment in tool box

- Storage methods of tools and equipment

- Insulation procedure

- Types of insulation

- Types of calibration

- Methods of equipment calibration

- Methods of tools and equipment inventory

- Report writing of faulty tools and equipment

- Define conductor.

- Differentiate between cable and wire.

- Describe the type of soldering.

- Differentiate between stripping and insulation removing.

- Describe the type of joints.

- Describe the procedure of jointing & soldering.

- Explain the composition of solder and soldering flux

- Define distribution board.

- Describe D.B. w.r.t. size, current rating, voltage, No. of C.Bs and phases etc.

- Name parts of distribution board.

- Define sensitivity of RCCB.

- Define MCB.

- Differentiate fuse and breaker.

- Define wiring accessories

- State purpose of each accessory.

- Types of cables

- Gauges of cables

- Single phase connection

- Types of joints

- Conductor and insulator

- Three phase connection

- Knowledge about cable gauging

- Knowledge about color code of cables / phase sequence.

- Methods of Wiring

- Types of wiring

- Types of connections

- Types of wiring tests

- Describe various wiring test

- Color of cables

- Distinguish between different    wiring systems

- Names of necessary materials required for each type of wiring.

- Uses of each type of wiring.

- Single pole switch.

- What is lamp?

- Single pole switch circuit and its use.

- Define current, voltage, power and resistance.

- Explain single pole switch socket circuit and its use.

- Define current, voltage, power and resistance.

- Describe socket.

- Explain two-way switch circuit and its use.

- Explain series circuit and its use.

- Define parallel circuit.

- Explain intermediate switch circuit and its use.

- Explain tunnel circuit and its use

- Explain impulse switch circuit and its use.

- Define push button.

- Define single pole switch.

- What is lamp?

- Explain single pole switch circuit and its use.

- Define current, voltage, power and resistance.

- Describe socket.

- Define series circuit.

- Define parallel circuit.

- Define impulse switch.

- Define power plug.

- Explain the function of exhaust

- Explain the function of AC and Heater.

- Explain multimedia.

- Explain Mic system.

- Explain Screen install on stage.

- Explain bell circuit

- Explain timer circuit.

- Explain fluorescent tube circuit

- Describe the safety of installation

- Explain the Protective measures against too high a contact voltage and conduct electrical accidents.

- Describe Fundamentals of installation engineering

- Describe the Power overhead-line systems.

- Describe Low-voltage switchgear and distribution systems.

- Explain Mounting and connection of motor testing of installed plant.

| SN | Tools |
| --- | --- |
| 1 | Electrician Tool kit. |
| 2 | Single pole switch. |
| 3 | Lamp holder |
| 4 | Lamp |
| 5 | Wooden/PVC board. |
| 6 | PVC Pipe/Duct. |
| 7 | PVC clamp. |
| 8 | Screw |
| 9 | PVC wire according to load. |
| 10 | Circuit Breaker. |
| 11 | AVO meter. |
| 12 | Test Indicator. |
| 13 | Exhaust |
| 14 | Fan |
| 15 | Series board. |
| 16 | Impulse switch. |
| 17 | Power plug |
| 18 | Cables |
| 19 | Wires. |
| 20 | Wire stripper. |
| 21 | Solder wire. |
| 22 | Soldering paste |
| 23 | Plier. |
| 24 | Nose plier. |
| 25 | Insulation remover. |
| 26 | Solder. |

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- To control domestic wiring of 3 rooms with single DB

### Perform Testing of Electrical Wiring

Overview:

This Competency Standard covers the skills and knowledge required to Perform Earth leakage Test, Perform Open Circuit Test, Perform Short Circuit Test, Perform Continuity/Loop Test, Perform Visual Test, Perform Insulation Test, Perform Polarity Test, Perform Earth Resistance Test, Perform Murray Loop Test, and Perform BLAVIER & Earth Loop Test. The module also focuses on maintaining green TVET concept by adopting 6 Rs of Green Skills I.e. Recycle, Reduce, Reuse, Renew, Repair, Rethink concepts.

| Competency Units | Performance Criteria |
| --- | --- |
| - Perform Earth leakage Test. | - Ensure the socket must be at least 13A for RCD plug in. - Adjust the sensitivity of RCD. - Ensure tripping time must not exceed than 200msec. - Plug the RCD in socket and switch on socket outlet. - Ensure P-N and P-E light up. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move the selection switch to 180o. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. - Move selection switch to 00. - Press the test button. - Ensure that RCD will trip and reading must be shown less than 200msec. |
| - Perform Open Circuit Test | - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect ohmmeter between starting and ending terminals of live conductor. - Ensure the reading must be near to 0 ohm. - Repeat P2 to P3 for neutral and earth conductor. |
| - Perform Short Circuit Test | - Disconnect the supply source, neutral conductor and earth conductor from distribution fuse box. - Connect one terminal of ohmmeter with live conductor. - Connect the other terminals of ohmmeter with neutral conductor. - Ensure the reading must be infinity (No reading). - Connect ohmmeter between live conductor and earth conductor. - Ensure the reading must be infinity (No reading) |
| - Perform Continuity/Loop Test | - Connect all metal clad switches, metal parts, conduits with earth. - Open the main switch. - Turn on all the switches. - Connect earth continuity tester with conduit and independent earth. - Measure the resistance value with tester which must not be more than 1 ohm. |
| - Perform Visual Test | - Check the wires joints. - Check if there is any spark. - Check over heating of wires. - Check all the appliances are on or fluctuating. - Check all indications of meters. - Check Voltages on all phases. - Check the DB and Breakers. - Check the main supply is coming properly. |
| - Perform Insulation Test | - Switch off the main breaker. - Short circuit all lighting connections. - Connect merger between line and earth. - Rotate the merger to generate the voltage. - Read the merger dial and ensure that the insulation resistance should not be less than 50M ohm of any single circuit. |
| - Perform Polarity Test | - Switch off the main switch. - Disconnect all loads. - Switch on all circuit control switches. - Connect ohm meter between main line and all the terminal of sockets and load points one by one. - Ensure meter reading value must be less than 1 ohm. |
| - Perform Earth Resistance Test | - Place 3 electrodes in earth at distance of 10m apart between every electrode. - Connect terminal E of earth resistance tester to first electrode. - Connect terminal P of earth resistance tester to the second electrode. - Connect terminal C of the earth resistance tester with third electrode. - Measure the resistances after applying specific voltage. - Repeat P1 to P5 by interacting earthling regions. - Ensure 3 readings must be equal. |
| - Perform Murray Loop Test | - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. |
| - Perform BLAVIER & Earth Loop Test | - Connect galvanometer with Wheatstone bridge. - Connect positive terminal of DC source with Wheatstone bridge. - Connect negative terminal of DC source with ground. - Connect remaining two terminal of Wheatstone bridge with two cores of the cable. - Short the other end of these two cores of cable. - Note the reading of galvanometer. - Calculate Rx. - Repeat the P1 to P7 for other cores of the cable. |

Knowledge & Understanding

- Define RCD

- Define sensitivity

- Explain P-E and P-N

- Explain the function of RCD.

- Explain the function of distribution box.

- Explain the function of fuse.

- Explain which meters are used for open circuit and short circuits test.

- What does it mean by 0 ohm reading in open circuit test?

- What does it mean by no reading?

- In short circuit test?

- Explain the purpose of continuity test.

- Explain the purpose of polarity test.

- Explain the purpose of insulation resistance test.

- Explain the purpose of Murray loop test.

- Explain the purpose of BLAVIER’s loop test.

- Describe why Wheatstone bridge is attached in Murray loop test.

- What is the purpose of DC supply in Murray loop test?

- Explain the purpose of Galvanometer.

Tools and Equipment

| SN | Tools |
| --- | --- |
| 1 | Sockets |
| 2 | RCD |
| 3 | Loads |
| 4 | Supply source |
| 5 | Distribution Box |
| 6 | Ohmmeter |
| 7 | Earth resistance tester |
| 8 | Continuity |
| 9 | Tester. |
| 10 | Breakers |
| 11 | Megger |

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Perform Murray Loop Test

### Install Security & Electrical Communication Systems

Overview:

This Competency Standard identifies the competencies required to install security & communication system in domestic and commercial buildings. The underpinning knowledge regarding the installation of Security & Communication System will be sufficient to provide the basis for your work. The module also focuses on maintaining green TVET concept by adopting 6 Rs of Green Skills i.e. Recycle, Reduce, Reuse, Renew, Repair, Rethink concepts.

| Competency Units | Performance Criteria |
| --- | --- |

CU1. Select the type of Safety / Security & Communication System

CU2.Install Safety / Security & Communication System

P1. Inspect the premises for installation of safety / security and communication system as per requirement

P2. Select the most appropriate safety / security/ communication system considering the practicality of the system, cost and client requirements

P1. Select Tools, test instruments & material as needed for the work

P2. Select Conduits/ trunk, cables, wire & switch gear and accessories according to the requirements

P3. Mark the Location for safety / security and communication fixtures for installation, Conduits / casing and capping laid / fixed according to the wiring diagram avoiding possible electrical interferences on other systems

P4. Lay the Wires / cables according to wiring diagram P5. Mount the safety / security and communication

P5. fixtures at the specified locations as per

manufacturer’s specifications and considering client’s

requirements

P6. Install the standby power back up system as per requirement

P5. Inform the client on the operating procedure and periodic testing of the system

recommended by the manufacturer.

P2. Adjust Settings, directions	where	necessary	for correct functioning of the system

P3. Check the standby power	backup	for	its proper functioning

P4. Perform testing of the system

the power source as

P1. Connect the system to

CU3. Test the Installed system

Knowledge & Understanding

The candidate must be able to demonstrate underpinning knowledge and understanding required to carry out the tasks covered in this competency standard. This includes the knowledge of:

- Circuit diagrams, service manuals, technical sketches, graphic symbols and wiring diagrams and manufacturer’s specifications etc.

- Types of electrical tools and its applications.

- Types of electronic test instruments used for testing safety/security and communication systems.

- Types of communication and power wires and cables used for safety /security and communication systems and their ratings.

- Types of security video cameras and sensing devices etc., used in safety/security and communication systems/devices.

- Importance of testing industrial safety/security and communication systems/devices after completion, and regular periodical inspections thereafter.

- Telecommunications Industry Association (TIA) / Pakistan Telecommunication Authority (PTA) regulations.

- Radio interference suppression techniques Record keeping and reporting.

Critical Evidence(s) Required

The candidate needs to produce following critical evidence(s) in order to be competent in this competency standard:

- Safety /security and communication circuits.

- Ring & radial Circuits for socket outlets.

- Circuits for fixed Safety /security and communication equipment/fixture.

List of Tools and Equipment

| SR. NO | NAME | QTY. REQUIRED |
| --- | --- | --- |
| 1 | Protection suits | 15 |
| 2 | Safety shoes | 15 |
| 3 | Safety goggles | 15 |
| 4 | Hearing protection | 15 |
| 5 | Respiratory mask | 20 |
| 6 | First Aid Box | 2 |
| 7 | First Aid Kit | 2 |
| 8 | Stretcher | 1 |
| 9 | Fire Buckets | 5 |
| 10 | Fire Extinguisher | 5 |
| 11 | Emergency Alarm/Bell | 3 |
| 12 | Emergency response Plan | 5 |
| 13 | Fall Protection Plan | 5 |
| 14 | Exhaust Fan | 5 |
| 15 | AVO meter. | 10 |
| 16 | Test Indicator | 20 |
| 17 | Electrician Tool kit. | 6 |
| 18 | Megger | 2 |
| 19 | Plier. | 20 |
| 20 | Nose plier. | 20 |
| 21 | Insulation remover. | 10 |
| 22 | Safety Helm | 20 |
| 23 | Specific Gravity Chart | 5 |
| 24 | Splicing Machine | 10 |
| 25 | Spring tension checking meter | 5 |
| 26 | Tachometer | 5 |
| 27 | Bearing Puller | 10 |
| 28 | Soldering Iron | 15 |
| 29 | Set of Screw Drivers | 15 |
| 30 | Circuit Boards | 30 |
| 31 | Safety Belt | 15 |
| 32 | Ring Spanner Set | 10 |
| 33 | RPM Meter | 15 |
| 34 | Ohmmeter | 20 |
| 35 | Earth resistance tester | 10 |
| 36 | Continuity tester | 20 |
| 37 | IR Temperature Gun | 10 |
| 38 | Mini Hydraulic Press Machine | 5 |
| 39 | OTDR Mete | 5 |
| 40 | Multimeter | 15 |
| 41 | Cable Knife | 15 |
| 42 | Phase Sequence Meter | 10 |
| 43 | Clamp Meter | 15 |
| 44 | L Scale | 10 |
| 45 | Lux Meter | 10 |
| 46 | Lugs Punching Machine (Hydraulic and Manual) | 5 |
| 47 | Cells tester | 10 |
| 48 | Micron Meter | 10 |
| 49 | Magnetic Conductor | 15 |
| 50 | Ammeter | 15 |
| 51 | Hydrometer | 15 |
| 52 | Disk Grinder | 10 |
| 53 | Handsaw | 15 |
| 54 | Hammer | 15 |
| 55 | Hacksaw cutter | 15 |
| 56 | Duct Rod | 15 |
| 57 | Battery Charger | 3 |
| 58 | Gloves Pair | 20 |
| 59 | Generator | 1 |
| 60 | Backup system | 1 |
| 61 | Flux | 5 |
| 62 | Filler gauge | 5 |
| 63 | Files (set) | 10 |
| 64 | Earth Tester | 2 |
| 65 | Battery Cleaning Kit | 2 |
| 66 | Bench Vice | 10 |
| 67 | Chisel | 15 |

List of Consumables

| SR.NO | NAME | QTY. REQUIRED |
| --- | --- | --- |
| 1 | Solder wire. | 2 KG |
| 2 | Soldering paste | 10 |
| 3 | Grinder Disks | 15 |
| 4 | PVC Pipe/Duct. | 5 each size |
| 5 | PVC clamp. | 5 boxes |
| 6 | Wooden/PVC board. | 10 sheets |
| 7 | Distribution Box | 5 |
| 8 | Circuit Breaker. | 5 each size |
| 9 | Screw | 5 boxes |
| 10 | Single pole switch. | 25 |
| 11 | Lamp holder | 20 |
| 12 | Lamp | 100 |
| 13 | Series board. | 10 |
| 14 | Impulse switch. | 10 |
| 15 | Power plug | 10 |
| 16 | Sockets | 15 |
| 17 | RCD | 15 |
| 18 | Loads | 10 |
| 19 | Supply source | 8 |
| 20 | Cables PVC single core and multicore | 5 meter each size |
| 21 | Wires single core | 3 rolls each size |
| 22 | Wire stripper | 20 |
| 23 | Hole saw | 10 |
| 24 | Hacksaw Blade | 30 |
| 25 | Drill bits | 15 each size |
| 26 | Electrical pvc tapes | 200 |
| 27 | Two way switch | 25 |
| 28 | Two pole switch | 25 |
| 29 | Junction Box | 25 |